## Table D1A
COA | General description | Component | Cost
20 | Capitalised direct costs |  | 2170984
21 | Structures and improvements |  | 481786
22 | Reactor plant equipment |  | 727316
23 | Turbine plant equipment |  | 537068
24 | Electric plant equipment |  | 195175
25 | Heat rejection system |  | 117554
26 | Miscellaneous plant equipment |  | 112085
30 | Capitalised indirect costs (not in COA 20) |  | 1322537
30 | Base construction costs |  | 3493513
40 | Capitalised owner's cost (assumed) |  | 300000
50 | Contingency (10%) |  | 379000
50 | Overnight construction cost |  | 4173000
50 | Overnight construction cost/kWe | Size of plant: 1 147 MWe | 3638

## Table D1B
COA (2-digit) | COA (3-digit) | General description | Component | Labour | Other | Labour Weights | Other Weights | Total Weights
21 | 21 | Structures and improvements | Total cost | 272432 | 209354 | 0.56546 | 0.43454 | 1
21 | 211 | Site preparation/yard work | Total | 34810 | 25172 | 0.58034 | 0.41966 | 0.1245
21 | 211 | Site preparation/yard work | Earthwork plus excavation work | 1822 | 881 | 0.67407 | 0.32593 | 0.0056104
21 | 211 | Site preparation/yard work | Roads, walks and parking areas | 1761 | 1951 | 0.47441 | 0.52559 | 0.0077047
21 | 211 | Site preparation/yard work | Fencing and gates | 251 | 267 | 0.48456 | 0.51544 | 0.0010752
21 | 211 | Site preparation/yard work | Sanitary sewer facilities | 2241 | 1061 | 0.67868 | 0.32132 | 0.0068537
21 | 211 | Site preparation/yard work | Yard drainage storm sewers | 1081 | 2383 | 0.31207 | 0.68793 | 0.0071899
21 | 211 | Site preparation/yard work | Roadway and yard lighting | 962 | 776 | 0.55351 | 0.44649 | 0.0036074
21 | 211 | Site preparation/yard work | Settling basins | 204 | 372 | 0.35417 | 0.64583 | 0.0011956
21 | 211 | Site preparation/yard work | Railroads | 3653 | 3391 | 0.5186 | 0.4814 | 0.014621
21 | 211 | Site preparation/yard work | Structure associated open cut | 11600 | 4013 | 0.74297 | 0.25703 | 0.032407
21 | 211 | Site preparation/yard work | Structure associated fill/backfill | 11236 | 10078 | 0.52717 | 0.47283 | 0.04424
21 | 212 | Reactor building | Total | 85504 | 70102 | 0.54949 | 0.45051 | 0.32298
21 | 212 | Reactor building | Substructure concrete | 6385 | 6083 | 0.51211 | 0.48789 | 0.025879
21 | 212 | Reactor building | Containment shell | 14861 | 8344 | 0.64042 | 0.35958 | 0.048165
21 | 212 | Reactor building | Containment dome | 6011 | 3479 | 0.6334 | 0.3666 | 0.019698
21 | 212 | Reactor building | Interior concrete | 24960 | 13692 | 0.64576 | 0.35424 | 0.080226
21 | 212 | Reactor building | Removable plugs | 438 | 178 | 0.71104 | 0.28896 | 0.0012786
21 | 212 | Reactor building | Structural and misc. steel | 1744 | 2949 | 0.37162 | 0.62838 | 0.0097408
21 | 212 | Reactor building | Containment liner | 19404 | 29914 | 0.39345 | 0.60655 | 0.10236
21 | 212 | Reactor building | Painting | 6622 | 1883 | 0.7786 | 0.2214 | 0.017653
21 | 212 | Reactor building | Plumbing and drains | 626 | 320 | 0.66173 | 0.33827 | 0.0019635
21 | 212 | Reactor building | Heating, ventilation and air conditioning (HVAC) | 40 | 188 | 0.17544 | 0.82456 | 0.00047324
21 | 212 | Reactor building | HVAC (safety-related) | 2302 | 1824 | 0.55793 | 0.44207 | 0.008564
21 | 212 | Reactor building | Lighting and service power | 2040 | 1031 | 0.66428 | 0.33572 | 0.0063742
21 | 212 | Reactor building | Elevator | 70 | 218 | 0.24306 | 0.75694 | 0.00059778
21 | 213 | Turbine generator building | Total | 26814 | 28751 | 0.48257 | 0.51743 | 0.11533
21 | 213 | Turbine generator building | Substructure concrete | 8238 | 4293 | 0.65741 | 0.34259 | 0.026009
21 | 213 | Turbine generator building | Superstructure | 14237 | 21667 | 0.39653 | 0.60347 | 0.074523
21 | 213 | Turbine generator building | Plumbing and drains | 2362 | 707 | 0.76963 | 0.23037 | 0.00637
21 | 213 | Turbine generator building | HVAC | 1043 | 1456 | 0.41737 | 0.58263 | 0.005187
21 | 213 | Turbine generator building | Lighting and service power | 874 | 412 | 0.67963 | 0.32037 | 0.0026692
21 | 213 | Turbine generator building | Elevator | 58 | 217 | 0.21091 | 0.78909 | 0.00057079
21 | 214 | Security building | Total | 2262 | 1006 | 0.69217 | 0.30783 | 0.0067831
21 | 214 | Security building | Substructure concrete | 134 | 79 | 0.62911 | 0.37089 | 0.00044211
21 | 214 | Security building | Superstructure | 1427 | 593 | 0.70644 | 0.29356 | 0.0041927
21 | 214 | Security building | Building services | 701 | 335 | 0.67664 | 0.32336 | 0.0021503
21 | 215 | Reactor services building | Total | 25248 | 19086 | 0.5695 | 0.4305 | 0.09202
21 | 215 | Reactor services building | Substructure concrete | 936 | 795 | 0.54073 | 0.45927 | 0.0035929
21 | 215 | Reactor services building | Superstructure | 18142 | 9140 | 0.66498 | 0.33502 | 0.056627
21 | 215 | Reactor services building | Plumbing and drains | 1019 | 289 | 0.77905 | 0.22095 | 0.0027149
21 | 215 | Reactor services building | HVAC | 3910 | 7209 | 0.35165 | 0.64835 | 0.023079
21 | 215 | Reactor services building | HVAC (special) | 258 | 948 | 0.21393 | 0.78607 | 0.0025032
21 | 215 | Reactor services building | Lighting and service power | 874 | 361 | 0.70769 | 0.29231 | 0.0025634
21 | 215 | Reactor services building | Elevator | 110 | 344 | 0.24229 | 0.75771 | 0.00094233
21 | 216 | Radioactive waste building | Total | 21657 | 12825 | 0.62807 | 0.37193 | 0.071571
21 | 216 | Radioactive waste building | Substructure concrete | 1953 | 1496 | 0.56625 | 0.43375 | 0.0071588
21 | 216 | Radioactive waste building | Superstructure | 16546 | 8792 | 0.65301 | 0.34699 | 0.052592
21 | 216 | Radioactive waste building | Plumbing and drains | 836 | 192 | 0.81323 | 0.18677 | 0.0021337
21 | 216 | Radioactive waste building | HVAC | 1627 | 1738 | 0.48351 | 0.51649 | 0.0069844
21 | 216 | Radioactive waste building | Lighting and service power | 583 | 258 | 0.69322 | 0.30678 | 0.0017456
21 | 216 | Radioactive waste building | Elevator | 111 | 349 | 0.2413 | 0.7587 | 0.00095478
21 | 217 | Fuel service building | Total | 10812 | 12898 | 0.45601 | 0.54399 | 0.049213
21 | 217 | Fuel service building | Substructure concrete | 2964 | 6832 | 0.30257 | 0.69743 | 0.020333
21 | 217 | Fuel service building | Superstructure | 6443 | 3156 | 0.67122 | 0.32878 | 0.019924
21 | 217 | Fuel service building | Plumbing and drains | 249 | 150 | 0.62406 | 0.37594 | 0.00082817
21 | 217 | Fuel service building | HVAC | 853 | 465 | 0.64719 | 0.35281 | 0.0027357
21 | 217 | Fuel service building | HVAC (special) | 99 | 2193 | 0.043194 | 0.95681 | 0.0047573
21 | 217 | Fuel service building | Lighting and service power | 204 | 103 | 0.6645 | 0.3355 | 0.00063721
21 | 218 | Other buildings | Total | 65324 | 39514 | 0.62309 | 0.37691 | 0.2176
21 | 218 | Other buildings | Earthwork plus excavation work | 758 | 439 | 0.63325 | 0.36675 | 0.0024845
21 | 218 | Other buildings | Substructure concrete | 5781 | 3703 | 0.60955 | 0.39045 | 0.019685
21 | 218 | Other buildings | Superstructure | 45031 | 25443 | 0.63897 | 0.36103 | 0.14628
21 | 218 | Other buildings | Elevator | 29 | 94 | 0.23577 | 0.76423 | 0.0002553
21 | 218 | Other buildings | Plumbing and drains | 3480 | 1314 | 0.72591 | 0.27409 | 0.0099505
21 | 218 | Other buildings | HVAC and HVAC (special) | 7239 | 7123 | 0.50404 | 0.49596 | 0.02981
21 | 218 | Other buildings | Lighting and service power | 2700 | 1186 | 0.6948 | 0.3052 | 0.0080658
21 | 218 | Other buildings | Building services | 304 | 212 | 0.58915 | 0.41085 | 0.001071
22 | 22 | Reactor plant equipment | Total cost | 117593 | 609723 | 0.16168 | 0.83832 | 1
22 | 221 | Reactor equipment | Total | 9033 | 188374 | 0.045758 | 0.95424 | 0.27142
22 | 221 | Reactor equipment | Reactor supports (field cost) | 1220 | 2074 | 0.37037 | 0.62963 | 0.004529
22 | 221 | Reactor equipment | Reactor vessel structure (NSSS allocation) | 0 | 68867 | 0 | 1 | 0.094686
22 | 221 | Reactor equipment | Reactor vessel structure (Field costs) | 5389 | 539 | 0.90908 | 0.090924 | 0.0081505
22 | 221 | Reactor equipment | Reactor lower internals (NSSS allocation) | 0 | 25825 | 0 | 1 | 0.035507
22 | 221 | Reactor equipment | Reactor lower internals (Field cost) | 794 | 79 | 0.90951 | 0.090493 | 0.0012003
22 | 221 | Reactor equipment | Reactor upper internals (NSSS allocation) | 0 | 25825 | 0 | 1 | 0.035507
22 | 221 | Reactor equipment | Reactor upper internals (Field cost) | 511 | 51 | 0.90925 | 0.090747 | 0.0007727
22 | 221 | Reactor equipment | Transport to site | 0 | 13292 | 0 | 1 | 0.018275
22 | 221 | Reactor equipment | Control rods (NSSS allocation) | 0 | 25825 | 0 | 1 | 0.035507
22 | 221 | Reactor equipment | Control rod drives (NSSS allocation) | 0 | 25825 | 0 | 1 | 0.035507
22 | 221 | Reactor equipment | Control rod drives (field cost) | 970 | 97 | 0.90909 | 0.090909 | 0.001467
22 | 221 | Reactor equipment | Control rod drive missile shield (field cost) | 111 | 11 | 0.90984 | 0.090164 | 0.00016774
22 | 221 | Reactor equipment | Control rod drive mechanism seismic supports (field cost) | 39 | 64 | 0.37864 | 0.62136 | 0.00014162
22 | 222 | Main heat transport system | Total | 15282 | 137599 | 0.09996 | 0.90004 | 0.2102
22 | 222 | Main heat transport system | Pumps, main coolant (NSSS allocation) | 0 | 38737 | 0 | 1 | 0.05326
22 | 222 | Main heat transport system | Fluid circulation drive (Field cost) | 3684 | 3553 | 0.50905 | 0.49095 | 0.0099503
22 | 222 | Main heat transport system | Piping, reactor coolant (NSSS allocation) | 0 | 19369 | 0 | 1 | 0.026631
22 | 222 | Main heat transport system | Piping, reactor coolant (Field cost) | 9586 | 4644 | 0.67365 | 0.32635 | 0.019565
22 | 222 | Main heat transport system | Steam generators (NSSS allocation) | 0 | 51650 | 0 | 1 | 0.071015
22 | 222 | Main heat transport system | Steam generator equipment (field cost) | 1774 | 241 | 0.8804 | 0.1196 | 0.0027705
22 | 222 | Main heat transport system | Pressurizer (NSSS allocation) | 0 | 12912 | 0 | 1 | 0.017753
22 | 222 | Main heat transport system | Pressurising system (field cost) | 237 | 36 | 0.86813 | 0.13187 | 0.00037535
22 | 222 | Main heat transport system | Pressurizer relief tank (NSSS allocation) | 0 | 6456 | 0 | 1 | 0.0088765
22 | 223 | Safety systems | Total | 13154 | 81208 | 0.1394 | 0.8606 | 0.12974
22 | 223 | Safety systems | Pumps and drives, residual heat removal (NSSS) | 0 | 12912 | 0 | 1 | 0.017753
22 | 223 | Safety systems | Heat exchanger, residual heat removal (NSSS) | 0 | 12912 | 0 | 1 | 0.017753
22 | 223 | Safety systems | Heat exchanger, residual heat removal (field cost) | 2954 | 2782 | 0.51499 | 0.48501 | 0.0078865
22 | 223 | Safety systems | Pumps and drives, safety injection system (NSSS) | 0 | 12912 | 0 | 1 | 0.017753
22 | 223 | Safety systems | Pumps and drives, safety injection system (Field costs) | 4791 | 3955 | 0.54779 | 0.45221 | 0.012025
22 | 223 | Safety systems | Accumulator tank (NSSS allocation) | 0 | 6456 | 0 | 1 | 0.0088765
22 | 223 | Safety systems | Boron injection tank (NSSS allocation) | 0 | 19368 | 0 | 1 | 0.026629
22 | 223 | Safety systems | Containment spray system | 4933 | 7790 | 0.38772 | 0.61228 | 0.017493
22 | 223 | Safety systems | Combustible gas control system | 476 | 2118 | 0.1835 | 0.8165 | 0.0035665
22 | 224 | Radioactive waste system | Total | 9631 | 40631 | 0.19162 | 0.80838 | 0.069106
22 | 224 | Liquid waste stream | Waste train, liquid equipment | 5050 | 7602 | 0.39915 | 0.60085 | 0.017395
22 | 224 | Liquid waste stream | Waste train, liquid, miscellaneous | 478 | 4396 | 0.098071 | 0.90193 | 0.0067014
22 | 224 | Liquid waste stream | Waste train, liquid, detergent | 55 | 1205 | 0.043651 | 0.95635 | 0.0017324
22 | 224 | Liquid waste stream | Waste train, liquid, chemical | 6 | 23 | 0.2069 | 0.7931 | 3.9873e-05
22 | 224 | Liquid waste stream | Steam generator blowdown, liquid waste | 1859 | 2437 | 0.43273 | 0.56727 | 0.0059066
22 | 224 | Liquid waste stream | Waste train, regenerated chemical liquids | 563 | 3188 | 0.15009 | 0.84991 | 0.0051573
22 | 224 | Liquid waste stream | Radwaste equipment, miscellaneous | 17 | 62 | 0.21519 | 0.78481 | 0.00010862
22 | 224 | Liquid waste stream | Waste, instrumentation and controls | 81 | 300 | 0.2126 | 0.7874 | 0.00052384
22 | 224 | Gas waste stream | Radwaste, gaseous (tritium) waste system | 418 | 3246 | 0.11408 | 0.88592 | 0.0050377
22 | 224 | Solid waste stream | Radwaste, solid, active dry volume reduction | 41 | 436 | 0.085954 | 0.91405 | 0.00065584
22 | 224 | Solid waste stream | Waste, solid volume reduction system | 1063 | 17737 | 0.056543 | 0.94346 | 0.025848
22 | 225 | Fuel handling systems | Total | 2059 | 27063 | 0.070703 | 0.9293 | 0.04004
22 | 225 | Fuel handling systems | Fuel handling tools and racks (NSSS allocation) | 0 | 21521 | 0 | 1 | 0.02959
22 | 225 | Fuel handling systems | Fuel handling tools and equipment | 928 | 2463 | 0.27367 | 0.72633 | 0.0046623
22 | 225 | Fuel handling systems | Fuel handling service platforms | 73 | 253 | 0.22393 | 0.77607 | 0.00044822
22 | 225 | Fuel handling systems | Fuel storage, cleaning and inspection equipment | 1058 | 2826 | 0.2724 | 0.7276 | 0.0053402
22 | 226 | Other reactor plant equipment | Total | 39682 | 72462 | 0.35385 | 0.64615 | 0.15419
22 | 226 | Other reactor plant equipment | Reactor inert gas system | 1131 | 1845 | 0.38004 | 0.61996 | 0.0040918
22 | 226 | Other reactor plant equipment | Reactor makeup water system | 1317 | 2265 | 0.36767 | 0.63233 | 0.004925
22 | 226 | Other reactor plant equipment | Reactor coolant treatment system | 0 | 19369 | 0 | 1 | 0.026631
22 | 226 | Other reactor plant equipment | Reactor chemical and volume control system | 11968 | 9348 | 0.56146 | 0.43854 | 0.029308
22 | 226 | Other reactor plant equipment | Boron recycle system | 3717 | 9308 | 0.28537 | 0.71463 | 0.017908
22 | 226 | Other reactor plant equipment | Reactor fluid leak detection system | 40 | 375 | 0.096386 | 0.90361 | 0.00057059
22 | 226 | Other reactor plant equipment | Reactor service water system | 13047 | 13802 | 0.48594 | 0.51406 | 0.036915
22 | 226 | Other reactor plant equipment | Reactor primary component cooling water | 7694 | 11948 | 0.39171 | 0.60829 | 0.027006
22 | 226 | Other reactor plant equipment | Reactor maintenance equipment (NSSS and field cost) | 164 | 3263 | 0.047855 | 0.95214 | 0.0047118
22 | 226 | Other reactor plant equipment | Reactor sampling equipment | 603 | 939 | 0.39105 | 0.60895 | 0.0021201
22 | 227 | Reactor I&C | Total | 18497 | 54756 | 0.25251 | 0.74749 | 0.10072
22 | 227 | Reactor I&C | NSSS control board | 867 | 2506 | 0.25704 | 0.74296 | 0.0046376
22 | 227 | Reactor I&C | Heating, ventilation and air conditioning panels | 133 | 207 | 0.39118 | 0.60882 | 0.00046747
22 | 227 | Reactor I&C | Radwaste panels | 520 | 863 | 0.37599 | 0.62401 | 0.0019015
22 | 227 | Reactor I&C | Logic panels | 520 | 827 | 0.38604 | 0.61396 | 0.001852
22 | 227 | Reactor I&C | Instrument racks | 405 | 1078 | 0.2731 | 0.7269 | 0.002039
22 | 227 | Reactor I&C | Alarm system | 145 | 577 | 0.20083 | 0.79917 | 0.00099269
22 | 227 | Reactor I&C | Process computer | 829 | 6980 | 0.10616 | 0.89384 | 0.010737
22 | 227 | Reactor I&C | Radiological monitoring | 578 | 2313 | 0.19993 | 0.80007 | 0.0039749
22 | 227 | Reactor I&C | Neutron monitoring | 809 | 2643 | 0.23436 | 0.76564 | 0.0047462
22 | 227 | Reactor I&C | Instrumentation for accident monitoring | 87 | 319 | 0.21429 | 0.78571 | 0.00055822
22 | 227 | Reactor I&C | Reactor diagnostic system | 289 | 1048 | 0.21616 | 0.78384 | 0.0018383
22 | 227 | Reactor I&C | Containment atmosphere monitoring | 289 | 486 | 0.3729 | 0.6271 | 0.0010656
22 | 227 | Reactor I&C | Containment leak monitor | 145 | 250 | 0.36709 | 0.63291 | 0.00054309
22 | 227 | Reactor I&C | Failed fuel detection | 133 | 226 | 0.37047 | 0.62953 | 0.0004936
22 | 227 | Reactor I&C | Reactor power control | 578 | 2024 | 0.22214 | 0.77786 | 0.0035775
22 | 227 | Reactor I&C | Reactor protection system | 723 | 2431 | 0.22923 | 0.77077 | 0.0043365
22 | 227 | Reactor I&C | Engineered safety feature actuation system | 463 | 1422 | 0.24562 | 0.75438 | 0.0025917
22 | 227 | Reactor I&C | Standard NSSS valve package | 0 | 21521 | 0 | 1 | 0.02959
22 | 227 | Reactor I&C | Reactor plant instrumentation and control tubing | 8094 | 1271 | 0.86428 | 0.13572 | 0.012876
22 | 227 | Reactor I&C | TMI instrumentation | 2891 | 5764 | 0.33403 | 0.66597 | 0.0119
22 | 228 | Reactor plant misc. items | Total | 10255 | 7630 | 0.57339 | 0.42661 | 0.02459
22 | 228 | Reactor plant misc. items | Field painting | 1191 | 387 | 0.75475 | 0.24525 | 0.0021696
22 | 228 | Reactor plant misc. items | Qualification of welders | 6079 | 911 | 0.86967 | 0.13033 | 0.0096107
22 | 228 | Reactor plant misc. items | Pipe insulation | 1553 | 2510 | 0.38223 | 0.61777 | 0.0055863
22 | 228 | Reactor plant misc. items | Equipment insulation | 299 | 919 | 0.24548 | 0.75452 | 0.0016747
22 | 228 | Reactor plant misc. items | NSSS Insulation | 1135 | 2903 | 0.28108 | 0.71892 | 0.0055519
23 | 23 | Turbine plant equipment | Total cost | 100711 | 436358 | 0.18752 | 0.81248 | 1
23 | 231 | Turbine generator(s) | Total | 18317 | 303246 | 0.056962 | 0.94304 | 0.59874
23 | 231 | Turbine generator(s) | Turbine generator | 0 | 294887 | 0 | 1 | 0.54907
23 | 231 | Turbine generator(s) | Turbine generator, other | 10455 | 1045 | 0.90913 | 0.09087 | 0.021413
23 | 231 | Turbine generator(s) | Turbine generator, associated piping | 334 | 55 | 0.85861 | 0.14139 | 0.0007243
23 | 231 | Turbine generator(s) | Turbine generator pedestal | 3966 | 1740 | 0.69506 | 0.30494 | 0.010624
23 | 231 | Turbine generator(s) | Turbine generator reheater/moisture separator drain system and supports | 2354 | 3814 | 0.38165 | 0.61835 | 0.011485
23 | 231 | Turbine generator(s) | Turbine generator lubricating oil system | 414 | 903 | 0.31435 | 0.68565 | 0.0024522
23 | 231 | Turbine generator(s) | Turbine generator hydrogen storage system | 482 | 486 | 0.49793 | 0.50207 | 0.0018024
23 | 231 | Turbine generator(s) | Turbine generator CO2 storage system | 312 | 316 | 0.49682 | 0.50318 | 0.0011693
23 | 232 | Turbine generator(s) | There is no 232 in the GIF COA | 0 | 0 | #DIV/0! | #DIV/0! | 0
23 | 233 | Condensing systems | Total | 19342 | 50214 | 0.27808 | 0.72192 | 0.12951
23 | 233 | Condensing systems | Condenser equipment | 4651 | 27105 | 0.14646 | 0.85354 | 0.059128
23 | 233 | Condensing systems | Condensate system | 13473 | 15440 | 0.46598 | 0.53402 | 0.053835
23 | 233 | Condensing systems | Condenser gas removal system | 868 | 1789 | 0.32668 | 0.67332 | 0.0049472
23 | 233 | Condensing systems | Turbine bypass system | 0 | 579 | 0 | 1 | 0.0010781
23 | 233 | Condensing systems | Condensate polishing | 350 | 5301 | 0.061936 | 0.93806 | 0.010522
23 | 234 | Feed heating system | Total | 17113 | 39500 | 0.30228 | 0.69772 | 0.10541
23 | 234 | Feed heating system | Feed water heaters | 1438 | 10275 | 0.12277 | 0.87723 | 0.021809
23 | 234 | Feed heating system | Feed water system | 11250 | 22694 | 0.33143 | 0.66857 | 0.063202
23 | 234 | Feed heating system | Feed water steam extraction system | 1928 | 2200 | 0.46705 | 0.53295 | 0.0076862
23 | 234 | Feed heating system | Feed water heater vent and drain system | 2497 | 4331 | 0.3657 | 0.6343 | 0.012713
23 | 235 | Other turbine plant equipment | Total | 23859 | 29717 | 0.44533 | 0.55467 | 0.099756
23 | 235 | Other turbine plant equipment | Turbine main vapour piping system | 15848 | 16676 | 0.48727 | 0.51273 | 0.060558
23 | 235 | Other turbine plant equipment | Turbine auxiliaries | 40 | 24 | 0.625 | 0.375 | 0.00011917
23 | 235 | Other turbine plant equipment | Turbine closed cooling water system | 4812 | 6972 | 0.40835 | 0.59165 | 0.021941
23 | 235 | Other turbine plant equipment | Turbine demineralised water makeup system | 2344 | 4901 | 0.32353 | 0.67647 | 0.01349
23 | 235 | Other turbine plant equipment | Turbine chemical treatment system | 66 | 173 | 0.27615 | 0.72385 | 0.00044501
23 | 235 | Other turbine plant equipment | Turbine neutralisation system | 749 | 971 | 0.43547 | 0.56453 | 0.0032026
23 | 236 | Turbine-Gen. I&C | Total | 11020 | 5430 | 0.66991 | 0.33009 | 0.030629
23 | 236 | Turbine-Gen. I&C | Turbine process I&C equipment | 2636 | 4126 | 0.38983 | 0.61017 | 0.012591
23 | 236 | Turbine-Gen. I&C | Turbine plant instrumentation and control tubing | 8383 | 1304 | 0.86539 | 0.13461 | 0.018037
23 | 237 | Turbine plant misc. items | Total | 11060 | 8250 | 0.57276 | 0.42724 | 0.035954
23 | 237 | Turbine plant misc. items | Field painting | 2516 | 665 | 0.79095 | 0.20905 | 0.0059229
23 | 237 | Turbine plant misc. items | Qualification of welders | 3648 | 546 | 0.86981 | 0.13019 | 0.0078091
23 | 237 | Turbine plant misc. items | Turbine plant insulation | 4896 | 7039 | 0.41022 | 0.58978 | 0.022222
24 | 24 | Electric plant equipment | Total cost | 83451 | 111723 | 0.42757 | 0.57243 | 1
24 | 241 | Switchgear | Total | 1449 | 27222 | 0.050539 | 0.94946 | 0.1469
24 | 241 | Generator equipment | Generator load break switch | 73 | 3091 | 0.023072 | 0.97693 | 0.016211
24 | 241 | Generator equipment | Generator neutral grounding equipment | 81 | 16 | 0.83505 | 0.16495 | 0.00049699
24 | 241 | Generator equipment | Transformer: generator current and potential | 46 | 64 | 0.41818 | 0.58182 | 0.0005636
24 | 241 | Station service | Switchgear: 13.8 kV (non-class 1E) | 184 | 7881 | 0.022815 | 0.97719 | 0.041322
24 | 241 | Station service | Switchgear: 4.16 kV (non-class 1E) | 115 | 4031 | 0.027738 | 0.97226 | 0.021243
24 | 241 | Station service | Switchgear: 4.16 kV (class 1E) | 184 | 7977 | 0.022546 | 0.97745 | 0.041814
24 | 241 | Station service | Diesel generator sequence logic panels | 75 | 621 | 0.10776 | 0.89224 | 0.003566
24 | 241 | Station service | Switchgear: 480 V motor control (non-class 1E) | 345 | 1877 | 0.15527 | 0.84473 | 0.011385
24 | 241 | Station service | Switchgear: 480 V motor control (class 1E) | 345 | 1664 | 0.17173 | 0.82827 | 0.010293
24 | 242 | Station service equipment | Total | 3856 | 44536 | 0.079683 | 0.92032 | 0.24794
24 | 242 | Station service equipment | Transformers: start-up | 605 | 5346 | 0.10166 | 0.89834 | 0.030491
24 | 242 | Station service equipment | Switchgear: load centre (non-class 1E) | 656 | 3725 | 0.14974 | 0.85026 | 0.022447
24 | 242 | Station service equipment | Switchgear: load centre (class 1E) | 368 | 2359 | 0.13495 | 0.86505 | 0.013972
24 | 242 | Station service equipment | Transformers: load centre (non-class 1E) | 49 | 1017 | 0.045966 | 0.95403 | 0.0054618
24 | 242 | Station service equipment | Transformers: load centre (class 1E) | 25 | 607 | 0.039557 | 0.96044 | 0.0032381
24 | 242 | Station service equipment | Transformers: miscellaneous | 75 | 71 | 0.5137 | 0.4863 | 0.00074805
24 | 242 | Station service equipment | Switchgear: batteries (non-class 1E) | 74 | 249 | 0.2291 | 0.7709 | 0.0016549
24 | 242 | Station service equipment | Switchgear: batteries (class 1E) | 148 | 298 | 0.33184 | 0.66816 | 0.0022851
24 | 242 | Station service equipment | Switchgear: charger (non-class 1E) | 43 | 133 | 0.24432 | 0.75568 | 0.00090176
24 | 242 | Station service equipment | Switchgear: charger (class 1E) | 72 | 215 | 0.25087 | 0.74913 | 0.0014705
24 | 242 | Station service equipment | Diesel generator systems emergency | 1321 | 29198 | 0.043285 | 0.95672 | 0.15637
24 | 242 | Station service equipment | Diesel generator systems emergency TMI | 288 | 991 | 0.22518 | 0.77482 | 0.0065531
24 | 242 | Station service equipment | Switchgear: inverters (non-class 1E) | 6 | 207 | 0.028169 | 0.97183 | 0.0010913
24 | 242 | Station service equipment | Switchgear: inverters (class 1E) | 124 | 118 | 0.5124 | 0.4876 | 0.0012399
24 | 243 | Switchboards | Total | 847 | 4071 | 0.17222 | 0.82778 | 0.025198
24 | 243 | Switchboards | Generator/auxiliary power system control panel | 288 | 962 | 0.2304 | 0.7696 | 0.0064045
24 | 243 | Switchboards | Generator protective relay panel | 219 | 724 | 0.23224 | 0.76776 | 0.0048316
24 | 243 | Switchboards | Switchgear: technical and on-site system control panels | 86 | 1634 | 0.05 | 0.95 | 0.0088126
24 | 243 | Switchboards | Switchgear: AC distribution (non-class 1E) | 18 | 34 | 0.34615 | 0.65385 | 0.00026643
24 | 243 | Switchboards | Switchgear: AC distribution (class 1E) | 30 | 72 | 0.29412 | 0.70588 | 0.00052261
24 | 243 | Switchboards | Switchgear: DC distribution (non-class 1E) | 20 | 99 | 0.16807 | 0.83193 | 0.00060971
24 | 243 | Switchboards | Switchgear: DC distribution (class 1E) | 81 | 320 | 0.202 | 0.798 | 0.0020546
24 | 243 | Switchboards | Switchgear: misc. buttons panels and fuses | 105 | 225 | 0.31818 | 0.68182 | 0.0016908
24 | 244 | Protective service equipment | Total | 5982 | 4245 | 0.58492 | 0.41508 | 0.052399
24 | 244 | Protective service equipment | Protection: general station grounding system | 4353 | 1636 | 0.72683 | 0.27317 | 0.030685
24 | 244 | Protective service equipment | Protection: lightning | 178 | 176 | 0.50282 | 0.49718 | 0.0018138
24 | 244 | Protective service equipment | Protection: cathodic | 868 | 824 | 0.513 | 0.487 | 0.0086692
24 | 244 | Protective service equipment | Protection: heat tracing and freeze | 583 | 1609 | 0.26597 | 0.73403 | 0.011231
24 | 245 | Electrical raceway systems | Total | 43156 | 10368 | 0.80629 | 0.19371 | 0.27424
24 | 245 | Electrical raceway systems | Conduit: underground ducts (non-class 1E) | 1665 | 692 | 0.70641 | 0.29359 | 0.012076
24 | 245 | Electrical raceway systems | Conduit: underground ducts (class 1E) | 5740 | 2347 | 0.70978 | 0.29022 | 0.041435
24 | 245 | Electrical raceway systems | Conduit: cable tray | 7480 | 3094 | 0.7074 | 0.2926 | 0.054177
24 | 245 | Electrical raceway systems | Conduit: miscellaneous | 28271 | 4236 | 0.86969 | 0.13031 | 0.16655
24 | 246 | Power and control cables and wiring | Total | 28161 | 21281 | 0.56958 | 0.43042 | 0.25332
24 | 246 | Power and control cables and wiring | Wiring and cables: generator circuits wiring | 1317 | 2252 | 0.36901 | 0.63099 | 0.018286
24 | 246 | Power and control cables and wiring | Wiring and cables: station service power | 3519 | 2969 | 0.54239 | 0.45761 | 0.033242
24 | 246 | Power and control cables and wiring | Wiring and cables: control cable | 11839 | 7904 | 0.59966 | 0.40034 | 0.10116
24 | 246 | Power and control cables and wiring | Wiring and cables: instrument wire | 10651 | 6393 | 0.62491 | 0.37509 | 0.087327
24 | 246 | Power and control cables and wiring | Wiring and cables: containment penetrations | 835 | 1762 | 0.32152 | 0.67848 | 0.013306
25 | 25 | Heat rejection system | Total cost | 36672 | 80882 | 0.31196 | 0.68804 | 1
25 | 251 | Heat rejection structures | Total | 6437 | 3961 | 0.61906 | 0.38094 | 0.088453
25 | 251 | Heat rejection structures | Cooling: makeup water intake structure | 1537 | 912 | 0.6276 | 0.3724 | 0.020833
25 | 251 | Heat rejection structures | Cooling: circulating water pump house structure | 3183 | 1336 | 0.70436 | 0.29564 | 0.038442
25 | 251 | Heat rejection structures | Cooling: circulating water pump house services | 201 | 302 | 0.3996 | 0.6004 | 0.0042789
25 | 251 | Heat rejection structures | Cooling: makeup water pre-treat. building | 1238 | 1172 | 0.51369 | 0.48631 | 0.020501
25 | 251 | Heat rejection structures | Cooling: makeup water pre-treat. building services | 279 | 241 | 0.53654 | 0.46346 | 0.0044235
25 | 252 | Heat rejection equipment | Total | 30235 | 76921 | 0.28216 | 0.71784 | 0.91155
25 | 252 | Heat rejection equipment | Cooling: water intake equipment | 230 | 883 | 0.20665 | 0.79335 | 0.009468
25 | 252 | Heat rejection equipment | Cooling: circulating water system | 11700 | 21778 | 0.34948 | 0.65052 | 0.28479
25 | 252 | Heat rejection equipment | Cooling towers | 17792 | 51287 | 0.25756 | 0.74244 | 0.58764
25 | 252 | Heat rejection equipment | Cooling tower basins | 99 | 98 | 0.50254 | 0.49746 | 0.0016758
25 | 252 | Heat rejection equipment | Cooling tower makeup/blowdown system | 414 | 2875 | 0.12587 | 0.87413 | 0.027979
26 | 26 | Miscellaneous equipment | Total cost 54 414 | 0 | 57671 | 0 | 1 | 1
26 | 261 | Transportation and lift equipment | Total | 2039 | 12347 | 0.14174 | 0.85826 | 0.24945
26 | 261 | Transportation and lift equipment | Cranes: overhead in turbine building | 350 | 3089 | 0.10177 | 0.89823 | 0.059631
26 | 261 | Transportation and lift equipment | Cranes in heater bay | 146 | 1236 | 0.10564 | 0.89436 | 0.023964
26 | 261 | Transportation and lift equipment | Cranes in reactor containment building | 993 | 6207 | 0.13792 | 0.86208 | 0.12485
26 | 261 | Transportation and lift equipment | Cranes: misc. with hoists and monorails | 467 | 780 | 0.3745 | 0.6255 | 0.021623
26 | 261 | Transportation and lift equipment | Cranes in diesel building | 82 | 1034 | 0.073477 | 0.92652 | 0.019351
26 | 262 | Air, water, plant fuel oil and steam services | Total | 37373 | 31568 | 0.5421 | 0.4579 | 1.1954
26 | 262 | Air, water, plant fuel oil and steam services | Misc. system: compressed air | 3206 | 1549 | 0.67424 | 0.32576 | 0.08245
26 | 262 | Air, water, plant fuel oil and steam services | Containment bldg. instrument air system | 6139 | 2847 | 0.68317 | 0.31683 | 0.15581
26 | 262 | Air, water, plant fuel oil and steam services | Service water system | 4668 | 5093 | 0.47823 | 0.52177 | 0.16925
26 | 262 | Air, water, plant fuel oil and steam services | Fire protection system | 17654 | 14528 | 0.54857 | 0.45143 | 0.55803
26 | 262 | Air, water, plant fuel oil and steam services | Misc. system: potable water system | 1150 | 1391 | 0.45258 | 0.54742 | 0.04406
26 | 262 | Air, water, plant fuel oil and steam services | Boiler, auxiliary system | 1657 | 2973 | 0.35788 | 0.64212 | 0.080283
26 | 262 | Air, water, plant fuel oil and steam services | Boiler, auxiliary feed water system | 54 | 166 | 0.24545 | 0.75455 | 0.0038147
26 | 262 | Air, water, plant fuel oil and steam services | Fuel oil system, auxiliary | 30 | 31 | 0.4918 | 0.5082 | 0.0010577
26 | 262 | Air, water, plant fuel oil and steam services | Aerator and makeup system, auxiliary | 59 | 155 | 0.2757 | 0.7243 | 0.0037107
26 | 262 | Air, water, plant fuel oil and steam services | Chemical feed system, auxiliary | 27 | 52 | 0.34177 | 0.65823 | 0.0013698
26 | 262 | Air, water, plant fuel oil and steam services | Condensate and steam return, auxiliary | 2304 | 2154 | 0.51682 | 0.48318 | 0.077301
26 | 262 | Air, water, plant fuel oil and steam services | Boiler blowdown, auxiliary | 9 | 41 | 0.18 | 0.82 | 0.00086699
26 | 262 | Air, water, plant fuel oil and steam services | Steam system complete I&C, auxiliary | 202 | 351 | 0.36528 | 0.63472 | 0.0095889
26 | 262 | Air, water, plant fuel oil and steam services | Fuel oil system, plant | 214 | 237 | 0.4745 | 0.5255 | 0.0078202
26 | 263 | Communications equipment | Total | 9296 | 6101 | 0.60375 | 0.39625 | 0.26698
26 | 263 | Communications equipment | Communication: telephone system | 262 | 158 | 0.62381 | 0.37619 | 0.0072827
26 | 263 | Communications equipment | Communication: public address and intercom | 1166 | 479 | 0.70881 | 0.29119 | 0.028524
26 | 263 | Communications equipment | Fire detection system communications | 2623 | 1339 | 0.66204 | 0.33796 | 0.0687
26 | 263 | Communications equipment | Security system communications | 5245 | 4125 | 0.55977 | 0.44023 | 0.16247
26 | 264 | Furnishings and fixtures | Total | 1206 | 5360 | 0.18367 | 0.81633 | 0.11385
26 | 264 | Furnishings and fixtures | Safety equipment | 16 | 34 | 0.32 | 0.68 | 0.00086699
26 | 264 | Furnishings and fixtures | Chemical laboratory shop | 422 | 2610 | 0.13918 | 0.86082 | 0.052574
26 | 264 | Furnishings and fixtures | Furnishings and office equipment | 9 | 316 | 0.027692 | 0.97231 | 0.0056354
26 | 264 | Furnishings and fixtures | Furnishings: change room equipment | 51 | 366 | 0.1223 | 0.8777 | 0.0072307
26 | 264 | Furnishings and fixtures | Environmental monitoring equipment | 657 | 1591 | 0.29226 | 0.70774 | 0.03898
26 | 264 | Furnishings and fixtures | Furnishings: dining facilities | 51 | 442 | 0.10345 | 0.89655 | 0.0085485
26 | 265 | Wastewater treatment equipment | Wastewater treatment equipment | 4500 | 2295 | 0.66225 | 0.33775 | 0.11782
30 | 30 | Capitalised indirect services | Total cost | 239437 | 1083101 | 0.18104 | 0.81896 | 1
31 | 31 | Design of plant at home office | Design of plant at home office, total | 0 | 482090 | 0 | 1
32 | 32 | Management at home office | Management at home office, including quality assurance | 0 | 28490 | 0 | 1
33 | 33 | Design services in field | Design services in field, assumed to be | 0 | 0 | #DIV/0! | #DIV/0!
34 | 34 | Construction management | Total | 5321 | 14626 | 0.26676 | 0.73324
34 | 34 | Construction management | Construction management cost | 0 | 14626 | 0 | 1
34 | 34 | Construction management | Construction site labour costs | 5321 | 0 | 1 | 0
35 | 35 | Field construction supervision | Total | 16282 | 175006 | 0.085118 | 0.91488
35 | 35 | Field construction supervision | Construction management cost | 0 | 175006 | 0 | 1
35 | 35 | Field construction supervision | Construction site labour costs | 16282 | 0 | 1 | 0
36 | 36 | Field indirect costs | Total | 217834 | 355848 | 0.37971 | 0.62029
36 | 36 | Field indirect costs | Construction: buildings, temp.: labour | 63725 | 0 | 1 | 0
36 | 36 | Field indirect costs | Construction: buildings, temp.: materials | 0 | 10226 | 0 | 1
36 | 36 | Field indirect costs | Construction: buildings, temp. facilities: labour | 133846 | 0 | 1 | 0
36 | 36 | Field indirect costs | Construction buildings, temp. facilities: materials | 0 | 36958 | 0 | 1
36 | 36 | Field indirect costs | Construction equip., major: labour | 17664 | 0 | 1 | 0
36 | 36 | Field indirect costs | Construction equip., major: materials | 0 | 69175 | 0 | 1
36 | 36 | Field indirect costs | Construction equip., small tools: labour costs | 571 | 0 | 1 | 0
36 | 36 | Field indirect costs | Construction equip., small tools: materials | 0 | 15293 | 0 | 1
36 | 36 | Field indirect costs | Construction: expendable materials | 0 | 19327 | 0 | 1
36 | 36 | Field indirect costs | Construction safety equip. inspection labour | 571 | 0 | 1 | 0
36 | 36 | Field indirect costs | Construction safety equip.: materials | 0 | 823 | 0 | 1
36 | 36 | Field indirect costs | Construction permits, insurance and local taxes | 0 | 27156 | 0 | 1
36 | 36 | Field indirect costs | Construction field office labour expenses | 1457 | 0 | 1 | 0
36 | 36 | Field indirect costs | Construction field office materials expenses | 0 | 27629 | 0 | 1
36 | 36 | Field indirect costs | Construction payroll insurance and taxes | 0 | 149261 | 0 | 1
37 | 37 | Plant commissioning | Plant commissioning, total | 0 | 27041 | 0 | 1

## Table D2
COA (2-digit) | COA (3-digit) | Component | NAICS Industry | CODE
22 | 223 | Accumulator tank (NSSS allocation) | Metal tank (heavy gauge) manufacturing | 332420
26 | 262 | Aerator and makeup system, auxiliary | Metal tank (heavy gauge) manufacturing | 332420
22 | 227 | Alarm system | Measuring and controlling device manufacturing | 334519
26 | 262 | Boiler blowdown, auxiliary | Power boiler and heat exchanger manufacturing | 332410
26 | 262 | Boiler, auxiliary feed water system | Power boiler and heat exchanger manufacturing | 332410
26 | 262 | Boiler, auxiliary system | Power boiler and heat exchanger manufacturing | 332410
22 | 223 | Boron injection system (NSSS allocation) | Power boiler and heat exchanger manufacturing | 332410
22 | 226 | Boron recycle system | Power boiler and heat exchanger manufacturing | 332410
21 | 210 | Building services | Power and related structures construction | 237130
26 | 262 | Chemical feed system, auxiliary | Metal tank (heavy gauge) manufacturing | 332420
26 | 264 | Chemical laboratory shop | Instruments and related products manufacturing | 334513
22 | 223 | Combustible gas control system | Instruments and related products manufacturing | 334513
26 | 263 | Communication: public address and intercom | Electrical and other wiring installation contractors | 238210
26 | 263 | Communication: telephone system | Electrical and other wiring installation contractors | 238210
21 | 212 | Concrete, interior | Concrete, poured structure contractors | 238110
26 | 262 | Condensate and steam return, auxiliary | Power boiler and heat exchanger manufacturing | 332410
23 | 233 | Condensate polishing | Power boiler and heat exchanger manufacturing | 332410
23 | 233 | Condensate system | Power boiler and heat exchanger manufacturing | 332410
23 | 233 | Condenser equip | Power boiler and heat exchanger manufacturing | 332410
23 | 233 | Condenser gas removal system | Power boiler and heat exchanger manufacturing | 332410
24 | 245 | Conduit: cable tray | Noncurrent-carrying wiring device manufacturing | 335932
24 | 245 | Conduit: miscellaneous | Noncurrent-carrying wiring device manufacturing | 335932
24 | 245 | Conduit: underground ducts (class 1E) | Noncurrent-carrying wiring device manufacturing | 335932
24 | 245 | Conduit: underground ducts (non-class 1E) | Noncurrent-carrying wiring device manufacturing | 335932
36 | 360 | Construction buildings, temp. facilities: materials | Labour, contracted | 561320
36 | 360 | Construction equip, major: labour | Labour, contracted | 561320
36 | 360 | Construction equip, major: materials | Power and related structures construction | 237130
36 | 360 | Construction equip, small tools: labour costs | Labour, contracted | 561320
36 | 360 | Construction equip, small tools: materials | Power and related structures construction | 237130
36 | 360 | Construction field office labour expenses | Labour, contracted | 561320
36 | 360 | Construction field office materials expenses | Power and related structures construction | 237130
30 | 300 | Construction management cost | Engineering services | 541330
36 | 360 | Construction payroll insurance and taxes | Insurance funds, other | 525190
36 | 360 | Construction permits, insurance and local taxes | Public finance activities (local) | 921130
36 | 360 | Construction safety equip: inspection | Labour, contracted | 561320
36 | 360 | Construction safety equip: materials | Power and related structures construction | 237130
30 | 300 | Construction site labour costs | Labour, contracted | 561320
36 | 360 | Construction: buildings, temporary facilities: labour | Labour, contracted | 561320
36 | 360 | Construction: buildings, temporary: labour | Labour, contracted | 561320
36 | 360 | Construction: buildings, temporary: materials | Power and related structures construction | 237130
36 | 360 | Construction: expendable materials | Power and related structures construction | 237130
22 | 227 | Containment atmosphere monitoring | Measuring and controlling device manufacturing | 334519
26 | 262 | Containment building instrument air system | Measuring and controlling device manufacturing | 334519
21 | 212 | Containment dome | Power and related structures construction | 237130
21 | 212 | Containment liner | Structural steel, fabricated, manufacturing | 332312
21 | 212 | Containment shell | Structural steel and precast concrete contractors | 238120
22 | 223 | Containment spray system | Industrial heating and cooling equipment manufacturing | 333415
22 | 221 | Control rod drive mechanism seismic supports (field cost) | Power boiler and heat exchanger manufacturing | 332410
22 | 221 | Control rod drive missile shield (field cost) | Power boiler and heat exchanger manufacturing | 332410
22 | 221 | Control rod drives (field cost) | Power boiler and heat exchanger manufacturing | 332410
22 | 221 | Control rod drives (NSSS allocation) | Power boiler and heat exchanger manufacturing | 332410
22 | 221 | Control rods (NSSS allocation) | Power boiler and heat exchanger manufacturing | 332410
25 | 252 | Cooling tower basins | Industrial heating and cooling equipment manufacturing | 333415
25 | 252 | Cooling tower makeup/blowdown system | Industrial heating and cooling equipment manufacturing | 333415
25 | 252 | Cooling towers | Industrial heating and cooling equipment manufacturing | 333415
25 | 251 | Cooling: circulating water pump house services | Pump and pumping equipment manufacturing | 333911
25 | 251 | Cooling: circulating water pump house structure | Power and related structures construction | 237130
25 | 252 | Cooling: circulating water system | Pump and pumping equipment manufacturing | 333911
25 | 251 | Cooling: makeup water intake structure | Pump and pumping equipment manufacturing | 333911
25 | 251 | Cooling: makeup water pre-treatment building | Pump and pumping equipment manufacturing | 333911
25 | 251 | Cooling: makeup water pre-treatment building services | Pump and pumping equipment manufacturing | 333911
25 | 252 | Cooling: water intake equip | Pump and pumping equipment manufacturing | 333911
26 | 261 | Cranes in diesel building | Crane, hoist and overhead travelling system manufacturing | 333923
26 | 261 | Cranes in heater bay | Crane, hoist and overhead travelling system manufacturing | 333923
26 | 261 | Cranes in reactor containment building | Crane, hoist and overhead travelling system manufacturing | 333923
26 | 261 | Cranes: misc. with hoists and monorails | Crane, hoist and overhead travelling system manufacturing | 333923
26 | 261 | Cranes: overhead in turbine building | Crane, hoist and overhead travelling system manufacturing | 333923
31 | 310 | Design of plant at home office, total | Engineering services | 541330
33 | 330 | Design services in field, total | Engineering services | 541330
24 | 241 | Diesel generator sequence logic panels | Instruments and related products manufacturing | 334513
24 | 242 | Diesel generator systems, emergency | Turbine and turbine generator set manufacturing | 333611
24 | 242 | Diesel generator systems, emergency TMI | Turbine and turbine generator set manufacturing | 333611
21 | 210 | Earthwork plus excavation work | Site preparation contractors | 238910
21 | 210 | Elevator | Elevator and moving stairway manufacturing | 333921
22 | 227 | Engineered safety feature actuation system | Measuring and controlling device manufacturing | 334519
26 | 264 | Environmental monitoring equipment | Instruments and related products manufacturing | 334513
22 | 228 | Equipment insulation | Building equipment contractors, other | 238290
22 | 227 | Failed fuel detection | Measuring and controlling device manufacturing | 334519
23 | 234 | Feed water heater vent and drain system | Pipe, iron and steel pipe and tube manufacturing | 331210
23 | 234 | Feed water heaters | Water treatment equipment manufacturing | 333318
23 | 234 | Feed water steam extraction system | Water treatment equipment manufacturing | 333318
23 | 234 | Feed water system | Pump and pumping equipment manufacturing | 333911
21 | 211 | Fencing and gates | Chain link fencing and fence gates | 332618
26 | 263 | Fire detection system, communications | Electrical and other wiring installation contractors | 238210
26 | 262 | Fire protection system | Fire detection and alarm systems manufacturing | 334290
22 | 222 | Fluid circulation drive (field cost) | Plumbing and HVAC contractors | 238220
26 | 262 | Fuel oil system, auxiliary | Metal tank (heavy gauge) manufacturing | 332420
26 | 262 | Fuel oil system, plant | Metal tank (heavy gauge) manufacturing | 332420
22 | 225 | Fuel storage, cleaning and inspection equipment | Measuring and controlling device manufacturing | 334519
26 | 264 | Furnishings and office equipment | Office furniture manufacturing | 337214
26 | 264 | Furnishings: change room equipment | Office furniture manufacturing | 337214
26 | 264 | Furnishings: dining facilities | Office furniture manufacturing | 337214
24 | 241 | Generator load break switch | Switchgear and switchboard apparatus manufacturing | 335313
24 | 241 | Generator neutral grounding equipment | Switchgear and switchboard apparatus manufacturing | 335313
24 | 243 | Generator protective relay panel | Switchgear and switchboard apparatus manufacturing | 335313
24 | 243 | Generator/auxiliary power system control panel | Switchgear and switchboard apparatus manufacturing | 335313
22 | 223 | Heat exchanger, residual heat removal (field cost) | Power and related structures construction | 237130
22 | 223 | Heat exchanger, residual heat removal (NSSS) | Power boiler and heat exchanger manufacturing | 332410
21 | 210 | HVAC | Plumbing and HVAC contractors | 238220
21 | 212 | HVAC (safety-related) | Plumbing and HVAC contractors | 238220
21 | 210 | HVAC (special) | Plumbing and HVAC contractors | 238220
22 | 227 | HVAC panels | Measuring and controlling device manufacturing | 334519
22 | 227 | Instrument racks | Measuring and controlling device manufacturing | 334519
22 | 227 | Instrumentation for accident monitoring | Measuring and controlling device manufacturing | 334519
21 | 210 | Lighting and service power | Electrical and other wiring installation contractors | 238210
22 | 227 | Logic panels | Measuring and controlling device manufacturing | 334519
32 | 320 | Management at home office, Including QA | Engineering services | 541330
26 | 262 | Misc. system: compressed air | Air compressors manufacturing | 333912
26 | 262 | Misc. system: potable water system | Water treatment equipment manufacturing | 333318
22 | 227 | Neutron monitoring | Measuring and controlling device manufacturing | 334519
22 | 227 | NSSS control board | Measuring and controlling device manufacturing | 334519
22 | 228 | NSSS Insulation | Building equipment contractors, other | 238290
20 | 200 | Painting, field | Painting engineered structures | 238320
22 | 228 | Pipe insulation | Building equipment contractors, other | 238290
22 | 222 | Piping, reactor coolant (field cost) | Power and related structures construction | 237130
22 | 222 | Piping, reactor coolant (NSSS allocation) | Pipe, iron and steel pipe and tube manufacturing | 331210
37 | 370 | Plant commissioning | Scientific and Technical Consulting Services | 541690
21 | 210 | Plumbing and drains | Metal products, all other misc. fabricated manufacturing | 332999
22 | 222 | Pressurising system (field cost) | Power and related structures construction | 237130
22 | 222 | Pressurizer (NSSS allocation) | Power boiler and heat exchanger manufacturing | 332410
22 | 222 | Pressurizer relief tank (NSSS allocation) | Metal tank (heavy gauge) manufacturing | 332420
22 | 227 | Process computer | Measuring and controlling device manufacturing | 334519
24 | 244 | Protection: cathodic | Electrical equipment and components, all other, manufacturing | 335999
24 | 244 | Protection: general station grounding system | Electrical equipment and components, all other, manufacturing | 335999
24 | 244 | Protection: heat tracing and freeze | Electrical equipment and components, all other, manufacturing | 335999
24 | 244 | Protection: lightning | Electrical equipment and components, all other, manufacturing | 335999
22 | 223 | Pumps and drives, residual heat removal (NSSS) | Pump and pumping equipment manufacturing | 333911
22 | 223 | Pumps and drives, safety injection system (field cost) | Pump and pumping equipment manufacturing | 333911
22 | 223 | Pumps and drives, safety injection system (NSSS) | Pump and pumping equipment manufacturing | 333911
20 | 200 | Qualification of welders | Welding, on-site, contractors | 238190
22 | 227 | Radiological monitoring | Measuring and controlling device manufacturing | 334519
22 | 224 | Radwaste equipment, miscellaneous | Other industrial machinery manufacturing | 333249
22 | 227 | Radwaste panels | Measuring and controlling device manufacturing | 334519
22 | 224 | Radwaste, gaseous (tritium) waste system | Other industrial machinery manufacturing | 333249
22 | 224 | Radwaste, solid, active dry volume reduction | Other industrial machinery manufacturing | 333249
21 | 211 | Railroads (hardware) | Heavy and other civil engineering construction | 237990
22 | 226 | Reactor chemical and volume control system | Instruments and related products manufacturing | 334513
22 | 226 | Reactor coolant treatment system | Water treatment equipment manufacturing | 333318
22 | 227 | Reactor diagnostic system | Measuring and controlling device manufacturing | 334519
22 | 226 | Reactor fluid leak detection system | Instruments and related products manufacturing | 334513
22 | 226 | Reactor inert gas system | Instruments and related products manufacturing | 334513
22 | 221 | Reactor lower internals (field cost) | Power and related structures construction | 237130
22 | 221 | Reactor lower internals (NSSS allocation) | Power boiler and heat exchanger manufacturing | 332410
22 | 226 | Reactor maintenance equip (NSSS and field cost) | Power boiler and heat exchanger manufacturing | 332410
22 | 226 | Reactor makeup water system | Pump and pumping equipment manufacturing | 333911
22 | 227 | Reactor plant I&C tubing | Noncurrent-carrying wiring device manufacturing | 335932
22 | 227 | Reactor power control | Measuring and controlling device manufacturing | 334519
22 | 226 | Reactor primary component cooling water | Pump and pumping equipment manufacturing | 333911
22 | 227 | Reactor protection system | Measuring and controlling device manufacturing | 334519
22 | 226 | Reactor sampling equipment | Instruments and related products manufacturing | 334513
22 | 226 | Reactor service water system | Pump and pumping equipment manufacturing | 333911
22 | 221 | Reactor supports (field cost) | Power and related structures construction | 237130
22 | 221 | Reactor upper internals (field cost) | Power and related structures construction | 237130
22 | 221 | Reactor upper internals (NSSS allocation) | Power boiler and heat exchanger manufacturing | 332410
22 | 221 | Reactor vessel structure (field cost) | Power and related structures construction | 237130
22 | 221 | Reactor vessel structure (NSSS allocation) | Power boiler and heat exchanger manufacturing | 332410
21 | 212 | Removable plugs | Metal products, all other misc. fabricated manufacturing | 332999
21 | 211 | Roads, walks and parking areas | Highway, street and bridge construction | 237310
21 | 211 | Roadway and yard lighting | Electrical and other wiring installation contractors | 238210
26 | 264 | Safety equipment | Instruments and related products manufacturing | 334513
21 | 211 | Sanitary sewer facilities | Water and sewer line and related structures construction | 237110
26 | 263 | Security system, communications | Electrical and other wiring installation contractors | 238210
26 | 262 | Service water system | Water treatment equipment manufacturing | 333318
21 | 211 | Settling basins | Power and related structures construction | 237130
22 | 227 | Standard NSSS valve package | Valve, industrial manufacturing | 332911
22 | 224 | Steam generator blowdown, liquid waste | Power boiler and heat exchanger manufacturing | 332410
22 | 222 | Steam generator equipment (field cost) | Power and related structures construction | 237130
22 | 222 | Steam generators (NSSS allocation) | Power boiler and heat exchanger manufacturing | 332410
26 | 262 | Steam system complete I&C, auxiliary | Instruments and related products manufacturing | 334513
21 | 212 | Structural and miscellaneous steel | Structural steel, fabricated, manufacturing | 332312
21 | 211 | Structure associated fill/backfill | Site preparation contractors | 238910
21 | 211 | Structure associated open cut | Site preparation contractors | 238910
24 | 241 | Switchgear: 13.8 kV (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 241 | Switchgear: 4.16 kV (class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 241 | Switchgear: 4.16 kV (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 241 | Switchgear: 480 V motor control (class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 241 | Switchgear: 480 V motor control (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 243 | Switchgear: AC distribution (class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 243 | Switchgear: AC distribution (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 242 | Switchgear: batteries (class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 242 | Switchgear: batteries (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 242 | Switchgear: charger (class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 242 | Switchgear: charger (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 243 | Switchgear: DC distribution (class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 243 | Switchgear: DC distribution (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 242 | Switchgear: inverters (class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 242 | Switchgear: inverters (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 242 | Switchgear: load centre (class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 242 | Switchgear: load centre (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
24 | 243 | Switchgear: misc. buttons, panels and fuses | Switchgear and switchboard apparatus manufacturing | 335313
24 | 243 | Switchgear: technical and on-site system control panels | Switchgear and switchboard apparatus manufacturing | 335313
22 | 227 | TMI instrumentation | Measuring and controlling device manufacturing | 334519
24 | 241 | Transformer: generator current and potential | Transformers, power and specialty, manufacturing | 335311
24 | 242 | Transformers: load centre (class 1E) | Transformers, power and specialty, manufacturing | 335311
24 | 242 | Transformers: load centre (non-class 1E) | Transformers, power and specialty, manufacturing | 335311
24 | 242 | Transformers: miscellaneous | Transformers, power and specialty, manufacturing | 335311
24 | 242 | Transformers: station service and start-up | Transformers, power and specialty, manufacturing | 335311
22 | 221 | Transport to site | Railroad line-haul | 482111
23 | 235 | Turbine auxiliaries | Turbine and turbine generator set manufacturing | 333611
23 | 233 | Turbine bypass system | Turbine and turbine generator set manufacturing | 333611
23 | 235 | Turbine chemical treatment system | Water treatment equipment manufacturing | 333318
23 | 235 | Turbine closed cooling water system | Water treatment equipment manufacturing | 333318
23 | 235 | Turbine demineralised water makeup system | Water treatment equipment manufacturing | 333318
23 | 231 | Turbine generator | Turbine and turbine generator set manufacturing | 333611
23 | 231 | Turbine generator CO2 storage system | Turbine and turbine generator set manufacturing | 333611
23 | 231 | Turbine generator hydrogen storage system | Turbine and turbine generator set manufacturing | 333611
23 | 231 | Turbine generator lubricating oil system | Turbine and turbine generator set manufacturing | 333611
23 | 231 | Turbine generator pedestal | Turbine and turbine generator set manufacturing | 333611
23 | 231 | Turbine generator reheater/moisture separator drain system and supports | Turbine and turbine generator set manufacturing | 333611
23 | 231 | Turbine generator, associated piping | Pipe, iron and steel pipe and tube manufacturing | 331210
23 | 231 | Turbine generator, other costs | Turbine and turbine generator set manufacturing | 333611
23 | 235 | Turbine main vapour piping system | Pipe, iron and steel pipe and tube manufacturing | 331210
23 | 235 | Turbine neutralisation system | Water treatment equipment manufacturing | 333318
23 | 236 | Turbine plant I&C tubing | Noncurrent-carrying wiring device manufacturing | 335932
23 | 237 | Turbine plant insulation | Building equipment contractors, other | 238290
22 | 224 | Waste train, liquid, chemical | Other industrial machinery manufacturing | 333249
22 | 224 | Waste train, liquid, chemical | Other industrial machinery manufacturing | 333249
22 | 224 | Waste train, liquid, detergent | Other industrial machinery manufacturing | 333249
22 | 224 | Waste train, liquid, detergent | Other industrial machinery manufacturing | 333249
22 | 224 | Waste train, liquid, miscellaneous | Other industrial machinery manufacturing | 333249
22 | 224 | Waste train, liquid, miscellaneous | Other industrial machinery manufacturing | 333249
22 | 224 | Waste train, regenerated chemical liquids | Other industrial machinery manufacturing | 333249
22 | 224 | Waste train, regenerated chemical liquids | Other industrial machinery manufacturing | 333249
22 | 224 | Waste, I&C | Instruments and related products manufacturing | 334513
22 | 224 | Waste, solid volume reduction system | Other industrial machinery manufacturing | 333249
26 | 265 | Wastewater treatment equipment | Water treatment equipment manufacturing | 333318
24 | 246 | Wiring and cables: containment penetrations | Electrical and other wiring installation contractors | 238210
24 | 246 | Wiring and cables: control cable | Electrical and other wiring installation contractors | 238210
24 | 246 | Wiring and cables: generator circuits wiring | Electrical and other wiring installation contractors | 238210
24 | 246 | Wiring and cables: instrument wire | Electrical and other wiring installation contractors | 238210
24 | 246 | Wiring and cables: station service power wiring | Electrical and other wiring installation contractors | 238210
21 | 211 | Yard drainage storm sewers | Water and sewer line and related structures construction | 237110