## Small Table
COA | General description | Component | Cost
20 | Capitalised direct costs |  | 2 170 984
21 | Structures and improvements |  | 481 786
22 | Reactor plant equipment |  | 727 316
23 | Turbine plant equipment |  | 537 068
24 | Electric plant equipment |  | 195 175
25 | Heat rejection system |  | 117 554
26 | Miscellaneous plant equipment |  | 112 085
| Capitalised indirect costs (not in COA 20) |  | 1 322 537
30
| Base construction costs |  | 3 493 513
40 | Capitalised owner's cost (assumed) |  | 300 000
| Contingency (10%) |  | 379 000
50 | Overnight construction cost |  | 4 173 000
| Overnight construction cost/kWe | Size of plant: 1 147 MWe | 3 638

## Large Table
21 | Structures and improvements | Total cost 272 432 | 209 354 | COA General description | Component | Unnamed: 0 | Labour | Other | Unnamed: 1 | 22 Reactor plant equipment | Total cost | 117 593 | 609 723 | 224 Radioactive waste system | Total | 9 631 | 40 631 | COA | General description | Component Labour
211 | Site preparation/yard work | Total 34 810 | 25 172
|  | Earthwork plus excavation work 1 822 | 881
|  | Roads, walks and parking areas 1 761 | 1 951
|  | Fencing and gates 251 | 267
|  | Sanitary sewer facilities 2 241 | 1 061
|  | Yard drainage storm sewers 1 081 | 2 383
|  | Roadway and yard lighting 962 | 776
|  | Settling basins 204 | 372
|  | Railroads 3 653 | 3 391
|  | Structure associated open cut 11 600 | 4 013
|  | Structure associated fill/backfill 11 236 | 10 078
212 | Reactor building | Total 85 504 | 70 102
|  | Substructure concrete 6 385 | 6 083
|  | Containment shell 14 861 | 8 344
|  | Containment dome 6 011 | 3 479
|  | Interior concrete 24 960 | 13 692
|  | Removable plugs 438 | 178
|  | Structural and misc. steel 1 744 | 2 949
|  | Containment liner 19 404 | 29 914
|  | Painting 6 622 | 1 883
|  | Plumbing and drains 626 | 320
|  | Heating, ventilation and air conditioning (HVAC) 40 | 188
|  | HVAC (safety-related) 2 302 | 1 824
|  | Lighting and service power 2 040 | 1 031
|  | Elevator 70 | 218
213 | Turbine generator building | Total 26 814 | 28 751
|  | Substructure concrete 8 238 | 4 293
|  | Superstructure 14 237 | 21 667
|  | Plumbing and drains 2 362 | 707
|  | HVAC 1 043 | 1 456
|  | Lighting and service power 874 | 412
|  | Elevator 58 | 217
214 | Security building | Total 2 262 | 1 006
|  | Substructure concrete 134 | 79
|  | Superstructure 1 427 | 593
|  | Building services 701 | 335
60 |  | MEASURING EMPLOYMENT GENERATED BY THE NUCLEAR POWER SECTOR, NEA No. 7204, © OECD 2018
|  |  |  | 215 Reactor services building | Total |  | 25 248 | 19 086
[5 empty] | Substructure concrete |  | 936 | 795
[5 empty] | Superstructure |  | 18 142 | 9 140
[5 empty] | Plumbing and drains |  | 1 019 | 289
[5 empty] | HVAC |  | 3 910 | 7 209
[5 empty] | HVAC (special) |  | 258 | 948
[5 empty] | Lighting and service power |  | 874 | 361
[5 empty] | Elevator |  | 110 | 344
|  |  |  | 216 Radioactive waste building | Total |  | 21 657 | 12 825
[5 empty] | Substructure concrete |  | 1 953 | 1 496
[5 empty] | Superstructure |  | 16 546 | 8 792
[5 empty] | Plumbing and drains |  | 836 | 192
[5 empty] | HVAC |  | 1 627 | 1 738
[5 empty] | Lighting and service power |  | 583 | 258
[5 empty] | Elevator |  | 111 | 349
|  |  |  | 217 Fuel service building | Total |  | 10 812 | 12 898
[5 empty] | Substructure concrete |  | 2 964 | 6 832
[5 empty] | Superstructure |  | 6 443 | 3 156
[5 empty] | Plumbing and drains |  | 249 | 150
[5 empty] | HVAC |  | 853 | 465
[5 empty] | HVAC (special) |  | 99 | 2 193
[5 empty] | Lighting and service power |  | 204 | 103
|  |  |  | 218 Other buildings | Total |  | 65 324 | 39 514
[5 empty] | Earthwork plus excavation work |  | 758 | 439
[5 empty] | Substructure concrete |  | 5 781 | 3 703
[5 empty] | Superstructure |  | 45 031 | 25 443
[5 empty] | Elevator |  | 29 | 94
[5 empty] | Plumbing and drains |  | 3 480 | 1 314
[5 empty] | HVAC and HVAC (special) |  | 7 239 | 7 123
[5 empty] | Lighting and service power |  | 2 700 | 1 186
[5 empty] | Building services |  | 304 | 212
|  |  |  | MEASURING EMPLOYMENT GENERATED BY THE NUCLEAR POWER SECTOR, NEA No. 7204, © OECD 2018 |  |  |  |  | 61
[10 empty] | 221 Reactor equipment | Total | 9 033 | 188 374
[11 empty] | Reactor supports (field cost) | 1 220 | 2 074
[11 empty] | Reactor vessel structure (NSSS allocation) | 0 | 68 867
[11 empty] | Reactor vessel structure (Field costs) | 5 389 | 539
[11 empty] | Reactor lower internals (NSSS allocation) | 0 | 25 825
[11 empty] | Reactor lower internals (Field cost) | 794 | 79
[11 empty] | Reactor upper internals (NSSS allocation) | 0 | 25 825
[11 empty] | Reactor upper internals (Field cost) | 511 | 51
[11 empty] | Transport to site | 0 | 13 292
[11 empty] | Control rods (NSSS allocation) | 0 | 25 825
[11 empty] | Control rod drives (NSSS allocation) | 0 | 25 825
[11 empty] | Control rod drives (field cost) | 970 | 97
[11 empty] | Control rod drive missile shield (field cost) | 111 | 11
[11 empty] | Control rod drive mechanism seismic supports (field cost) | 39 | 64
[10 empty] | 222 Main heat transport system | Total | 15 282 | 137 599
[11 empty] | Pumps, main coolant (NSSS allocation) | 0 | 38 737
[11 empty] | Fluid circulation drive (Field cost) | 3 684 | 3 553
[11 empty] | Piping, reactor coolant (NSSS allocation) | 0 | 19 369
[11 empty] | Piping, reactor coolant (Field cost) | 9 586 | 4 644
[11 empty] | Steam generators (NSSS allocation) | 0 | 51 650
[11 empty] | Steam generator equipment (field cost) | 1 774 | 241
[11 empty] | Pressurizer (NSSS allocation) | 0 | 12 912
[11 empty] | Pressurising system (field cost) | 237 | 36
[11 empty] | Pressurizer relief tank (NSSS allocation) | 0 | 6 456
[10 empty] | 223 Safety systems | Total | 13 154 | 81 208
[11 empty] | Pumps and drives, residual heat removal (NSSS) | 0 | 12 912
[11 empty] | Heat exchanger, residual heat removal (NSSS) | 0 | 12 912
[11 empty] | Heat exchanger, residual heat removal (field cost) | 2 954 | 2 782
[11 empty] | Pumps and drives, safety injection system (NSSS) | 0 | 12 912
[11 empty] | Pumps and drives, safety injection system (Field costs) | 4 791 | 3 955
[11 empty] | Accumulator tank (NSSS allocation) | 0 | 6 456
[11 empty] | Boron injection tank (NSSS allocation) | 0 | 19 368
[11 empty] | Containment spray system | 4 933 | 7 790
[11 empty] | Combustible gas control system | 476 | 2 118
NSSS = Nuclear steam supply system.
[10 empty] | 62 |  | MEASURING EMPLOYMENT GENERATED BY THE NUCLEAR POWER SECTOR, NEA No. 7204, © OECD 2018
[14 empty] | Liquid waste stream | Waste train, liquid equipment | 5 050 | 7 602
[15 empty] | Waste train, liquid, miscellaneous | 478 | 4 396
[15 empty] | Waste train, liquid, detergent | 55 | 1 205
[15 empty] | Waste train, liquid, chemical | 6 | 23
[15 empty] | Steam generator blowdown, liquid waste | 1 859 | 2 437
[15 empty] | Waste train, regenerated chemical liquids | 563 | 3 188
[15 empty] | Radwaste equipment, miscellaneous | 17 | 62
[15 empty] | Waste, instrumentation and controls | 81 | 300
[14 empty] | Gas waste stream | Radwaste, gaseous (tritium) waste system | 418 | 3 246
[14 empty] | Solid waste stream | Radwaste, solid, active dry volume reduction | 41 | 436
[15 empty] | Waste, solid volume reduction system | 1 063 | 17 737
[14 empty] | 225 Fuel handling systems | Total | 2 059 | 27 063
[15 empty] | Fuel handling tools and racks (NSSS allocation) | 0 | 21 521
[15 empty] | Fuel handling tools and equipment | 928 | 2 463
[15 empty] | Fuel handling service platforms | 73 | 253
[15 empty] | Fuel storage, cleaning and inspection equipment | 1 058 | 2 826
[14 empty] | 226 Other reactor plant equipment | Total | 39 682 | 72 462
[15 empty] | Reactor inert gas system | 1 131 | 1 845
[15 empty] | Reactor makeup water system | 1 317 | 2 265
[15 empty] | Reactor coolant treatment system | 0 | 19 369
[15 empty] | Reactor chemical and volume control system | 11 968 | 9 348
[15 empty] | Boron recycle system | 3 717 | 9 308
[15 empty] | Reactor fluid leak detection system | 40 | 375
[15 empty] | Reactor service water system | 13 047 | 13 802
[15 empty] | Reactor primary component cooling water | 7 694 | 11 948
Reactor maintenance equipment
[16 empty] | 164 | 3 263
(NSSS and field cost)
[15 empty] | Reactor sampling equipment | 603 | 939
NSSS = Nuclear steam supply system.
[9 empty] | 63 |  |  |  |  | MEASURING EMPLOYMENT GENERATED BY THE NUCLEAR POWER SECTOR, NEA No. 7204, © OECD 2018
|  |  |  | 227 Reactor I&C | Total |  | 18 497 | 54 756
[5 empty] | NSSS control board |  | 867 | 2 506
[5 empty] | Heating, ventilation and air conditioning panels |  | 133 | 207
[5 empty] | Radwaste panels |  | 520 | 863
[5 empty] | Logic panels |  | 520 | 827
[5 empty] | Instrument racks |  | 405 | 1 078
[5 empty] | Alarm system |  | 145 | 577
[5 empty] | Process computer |  | 829 | 6 980
[5 empty] | Radiological monitoring |  | 578 | 2 313
[5 empty] | Neutron monitoring |  | 809 | 2 643
[5 empty] | Instrumentation for accident monitoring |  | 87 | 319
[5 empty] | Reactor diagnostic system |  | 289 | 1 048
[5 empty] | Containment atmosphere monitoring |  | 289 | 486
[5 empty] | Containment leak monitor |  | 145 | 250
[5 empty] | Failed fuel detection |  | 133 | 226
[5 empty] | Reactor power control |  | 578 | 2 024
[5 empty] | Reactor protection system |  | 723 | 2 431
[5 empty] | Engineered safety feature actuation system |  | 463 | 1 422
[5 empty] | Standard NSSS valve package |  | 0 | 21 521
[5 empty] | Reactor plant instrumentation and control tubing |  | 8 094 | 1 271
[5 empty] | TMI instrumentation |  | 2 891 | 5 764
|  |  |  | 228 Reactor plant misc. items | Total |  | 10 255 | 7 630
[5 empty] | Field painting |  | 1 191 | 387
[5 empty] | Qualification of welders |  | 6 079 | 911
[5 empty] | Pipe insulation |  | 1 553 | 2 510
[5 empty] | Equipment insulation |  | 299 | 919
[5 empty] | NSSS Insulation |  | 1 135 | 2 903
I&C= Instrumentation and controls, NSSS = Nuclear steam supply system, TMI = post-Three Mile Island requirements.
|  |  |  | 64 | MEASURING EMPLOYMENT GENERATED BY THE NUCLEAR POWER SECTOR, NEA No. 7204, © OECD 2018
|  |  |  | 23 Turbine plant equipment | Total cost |  | 100 711 | 436 358
|  |  |  | 231 Turbine generator(s) | Total |  | 18 317 | 303 246
[5 empty] | Turbine generator |  | 0 | 294 887
[5 empty] | Turbine generator, other |  | 10 455 | 1 045
[5 empty] | Turbine generator, associated piping |  | 334 | 55
[5 empty] | Turbine generator pedestal |  | 3 966 | 1 740
Turbine generator reheater/moisture separator drain
[5 empty] | system and supports |  | 2 354 | 3 814
[5 empty] | Turbine generator lubricating oil system |  | 414 | 903
|  |  |  | 486 | Turbine generator hydrogen storage system |  | 482
[5 empty] | Turbine generator CO2 storage system |  | 312 | 316
|  |  |  | 232 | There is no 232 in the GIF COA
|  |  |  | 233 Condensing systems | Total |  | 19 342 | 50 214
[5 empty] | Condenser equipment |  | 4 651 | 27 105
[5 empty] | Condensate system |  | 13 473 | 15 440
[5 empty] | Condenser gas removal system |  | 868 | 1 789
[5 empty] | Turbine bypass system |  | 0 | 579
[5 empty] | Condensate polishing |  | 350 | 5 301
|  |  |  | 234 Feed heating system | Total |  | 17 113 | 39 500
[5 empty] | Feed water heaters |  | 1 438 | 10 275
[5 empty] | Feed water system |  | 11 250 | 22 694
[5 empty] | Feed water steam extraction system |  | 1 928 | 2 200
[5 empty] | Feed water heater vent and drain system |  | 2 497 | 4 331
|  |  |  | 235 Other turbine plant equipment | Total |  | 23 859 | 29 717
[5 empty] | Turbine main vapour piping system |  | 15 848 | 16 676
[5 empty] | Turbine auxiliaries |  | 40 | 24
[5 empty] | Turbine closed cooling water system |  | 4 812 | 6 972
[5 empty] | Turbine demineralised water makeup system |  | 2 344 | 4 901
[5 empty] | Turbine chemical treatment system |  | 66 | 173
[5 empty] | Turbine neutralisation system |  | 749 | 971
|  |  |  | 236 Turbine-Gen. I&C | Total |  | 11 020 | 5 430
[5 empty] | Turbine process I&C equipment |  | 2 636 | 4 126
[5 empty] | Turbine plant instrumentation and control tubing |  | 8 383 | 1 304
|  |  |  | 237 Turbine plant misc. items | Total |  | 11 060 | 8 250
[5 empty] | Field painting |  | 2 516 | 665
[5 empty] | Qualification of welders |  | 3 648 | 546
[5 empty] | Turbine plant insulation |  | 4 896 | 7 039
|  |  |  | MEASURING EMPLOYMENT GENERATED BY THE NUCLEAR POWER SECTOR, NEA No. 7204, © OECD 2018 |  |  |  |  | 65
[8 empty] | 111 723 | [9 empty] | 24 | Electric plant equipment | Total cost 83 451
[8 empty] | 27 222 | [9 empty] | 241 | Switchgear | Total 1 449
[8 empty] | 3 091 | [10 empty] | Generator equipment | Generator load break switch 73
[8 empty] | 16 | [11 empty] | Generator neutral grounding equipment 81
[8 empty] | 64 | [11 empty] | Transformer: generator current and potential 46
[8 empty] | 7 881 | [10 empty] | Station service | Switchgear: 13.8 kV (non-class 1E) 184
[8 empty] | 4 031 | [11 empty] | Switchgear: 4.16 kV (non-class 1E) 115
[8 empty] | 7 977 | [11 empty] | Switchgear: 4.16 kV (class 1E) 184
[8 empty] | 621 | [11 empty] | Diesel generator sequence logic panels 75
[8 empty] | 1 877 | [11 empty] | Switchgear: 480 V motor control (non-class 1E) 345
[8 empty] | 1 664 | [11 empty] | Switchgear: 480 V motor control (class 1E) 345
[8 empty] | 44 536 | [9 empty] | 242 | Station service equipment | Total 3 856
[8 empty] | 5 346 | [11 empty] | Transformers: start-up 605
[8 empty] | 3 725 | [11 empty] | Switchgear: load centre (non-class 1E) 656
[8 empty] | 2 359 | [11 empty] | Switchgear: load centre (class 1E) 368
[8 empty] | 1 017 | [11 empty] | Transformers: load centre (non-class 1E) 49
[8 empty] | 607 | [11 empty] | Transformers: load centre (class 1E) 25
[8 empty] | 71 | [11 empty] | Transformers: miscellaneous 75
[8 empty] | 249 | [11 empty] | Switchgear: batteries (non-class 1E) 74
[8 empty] | 298 | [11 empty] | Switchgear: batteries (class 1E) 148
[8 empty] | 133 | [11 empty] | Switchgear: charger (non-class 1E) 43
[8 empty] | 215 | [11 empty] | Switchgear: charger (class 1E) 72
[8 empty] | 29 198 | [11 empty] | Diesel generator systems emergency 1 321
[8 empty] | 991 | [11 empty] | Diesel generator systems emergency TMI 288
[8 empty] | 207 | [11 empty] | Switchgear: inverters (non-class 1E) 6
[8 empty] | 118 | [11 empty] | Switchgear: inverters (class 1E) 124
[8 empty] | 4 071 | [9 empty] | 243 | Switchboards | Total 847
[8 empty] | 962 | [11 empty] | Generator/auxiliary power system control panel 288
[8 empty] | 724 | [11 empty] | Generator protective relay panel 219
Switchgear: technical and on-site system control
[8 empty] | 1 634 | [11 empty] | panels 86
[8 empty] | 34 | [11 empty] | Switchgear: AC distribution (non-class 1E) 18
[8 empty] | 72 | [11 empty] | Switchgear: AC distribution (class 1E) 30
[8 empty] | 99 | [11 empty] | Switchgear: DC distribution (non-class 1E) 20
[8 empty] | 320 | [11 empty] | Switchgear: DC distribution (class 1E) 81
[8 empty] | 225 | [11 empty] | Switchgear: misc. buttons panels and fuses 105
[18 empty] | 66 |  | MEASURING EMPLOYMENT GENERATED BY THE NUCLEAR POWER SECTOR, NEA No. 7204, © OECD 2018
|  |  |  | 244 Protective service equipment | Total |  | 5 982 | 4 245
[5 empty] | Protection: general station grounding system |  | 4 353 | 1 636
[5 empty] | Protection: lightning |  | 178 | 176
[5 empty] | Protection: cathodic |  | 868 | 824
[5 empty] | Protection: heat tracing and freeze |  | 583 | 1 609
|  |  |  | 245 Electrical raceway systems | Total |  | 43 156 | 10 368
[5 empty] | Conduit: underground ducts (non-class 1E) |  | 1 665 | 692
[5 empty] | Conduit: underground ducts (class 1E) |  | 5 740 | 2 347
[5 empty] | Conduit: cable tray |  | 7 480 | 3 094
[5 empty] | Conduit: miscellaneous |  | 28 271 | 4 236
|  |  |  | 246 Power and control cables and | Total |  | 28 161 | 21 281
wiring
[5 empty] | Wiring and cables: generator circuits wiring |  | 1 317 | 2 252
[5 empty] | Wiring and cables: station service power |  | 3 519 | 2 969
[5 empty] | Wiring and cables: control cable |  | 11 839 | 7 904
[5 empty] | Wiring and cables: instrument wire |  | 10 651 | 6 393
[5 empty] | Wiring and cables: containment penetrations |  | 835 | 1 762
|  |  |  | 25 Heat rejection system | Total cost |  | 36 672 | 80 882
|  |  |  | 251 Heat rejection structures | Total |  | 6 437 | 3 961
[5 empty] | Cooling: makeup water intake structure |  | 1 537 | 912
[5 empty] | Cooling: circulating water pump house structure |  | 3 183 | 1 336
[5 empty] | Cooling: circulating water pump house services |  | 201 | 302
[5 empty] | Cooling: makeup water pre-treat. building |  | 1 238 | 1 172
[5 empty] | Cooling: makeup water pre-treat. building services |  | 279 | 241
|  |  |  | 252 Heat rejection equipment | Total |  | 30 235 | 76 921
[5 empty] | Cooling: water intake equipment |  | 230 | 883
[5 empty] | Cooling: circulating water system |  | 11 700 | 21 778
[5 empty] | Cooling towers |  | 17 792 | 51 287
[5 empty] | Cooling tower basins |  | 99 | 98
[5 empty] | Cooling tower makeup/blowdown system |  | 414 | 2 875
|  |  |  | MEASURING EMPLOYMENT GENERATED BY THE NUCLEAR POWER SECTOR, NEA No. 7204, © OECD 2018 |  |  |  |  | 67
[8 empty] | 57 671 | [9 empty] | 26 | Miscellaneous equipment | Total cost 54 414
[8 empty] | 12 347 | [9 empty] | 261 | Transportation and lift | Total 2 039
equipment
[8 empty] | 3 089 | [11 empty] | Cranes: overhead in turbine building 350
[8 empty] | 1 236 | [11 empty] | Cranes in heater bay 146
[8 empty] | 6 207 | [11 empty] | Cranes in reactor containment building 993
[8 empty] | 780 | [11 empty] | Cranes: misc. with hoists and monorails 467
[8 empty] | 1 034 | [11 empty] | Cranes in diesel building 82
[8 empty] | 31 568 | [9 empty] | 262 | Air, water, plant fuel oil and | Total 37 373
[8 empty] | 1 549 | [10 empty] | steam services | Misc. system: compressed air 3 206
[8 empty] | 2 847 | [11 empty] | Containment bldg. instrument air system 6 139
[8 empty] | 5 093 | [11 empty] | Service water system 4 668
[8 empty] | 14 528 | [11 empty] | Fire protection system 17 654
[8 empty] | 1 391 | [11 empty] | Misc. system: potable water system 1 150
[8 empty] | 2 973 | [11 empty] | Boiler, auxiliary system 1 657
[8 empty] | 166 | [11 empty] | Boiler, auxiliary feed water system 54
[8 empty] | 31 | [11 empty] | Fuel oil system, auxiliary 30
[8 empty] | 155 | [11 empty] | Aerator and makeup system, auxiliary 59
[8 empty] | 52 | [11 empty] | Chemical feed system, auxiliary 27
[8 empty] | 2 154 | [11 empty] | Condensate and steam return, auxiliary 2 304
[8 empty] | 41 | [11 empty] | Boiler blowdown, auxiliary 9
[8 empty] | 351 | [11 empty] | Steam system complete I&C, auxiliary 202
[8 empty] | 237 | [11 empty] | Fuel oil system, plant 214
[8 empty] | 6 101 | [9 empty] | 263 | Communications equipment | Total 9 296
[8 empty] | 158 | [11 empty] | Communication: telephone system 262
[8 empty] | 479 | [11 empty] | Communication: public address and intercom 1 166
[8 empty] | 1 339 | [11 empty] | Fire detection system communications 2 623
[8 empty] | 4 125 | [11 empty] | Security system communications 5 245
[8 empty] | 5 360 | [9 empty] | 264 | Furnishings and fixtures | Total 1 206
[8 empty] | 34 | [11 empty] | Safety equipment 16
[8 empty] | 2 610 | [11 empty] | Chemical laboratory shop 422
[8 empty] | 316 | [11 empty] | Furnishings and office equipment 9
[8 empty] | 366 | [11 empty] | Furnishings: change room equipment 51
[8 empty] | 1 591 | [11 empty] | Environmental monitoring equipment 657
[8 empty] | 442 | [11 empty] | Furnishings: dining facilities 51
[18 empty] | 265 | Wastewater treatment
[8 empty] | 2 295 | [10 empty] | equipment | Wastewater treatment equipment 4 500
[18 empty] | 68 |  | MEASURING EMPLOYMENT GENERATED BY THE NUCLEAR POWER SECTOR, NEA No. 7204, © OECD 2018
|  |  |  | 30 Capitalised indirect services | Total cost |  | 239 437 | 1 083 101
|  |  |  | 31 Design of plant at home office | Design of plant at home office, total |  | 0 | 482 090
|  |  |  | 32 Management at home office | Management at home office, including quality
[5 empty] | assurance, total |  | 0 | 28 490
|  |  |  | 33 Design services in field | Design services in field, assumed to be |  | 0 | 0
|  |  |  | 34 Construction management | Total |  | 5 321 | 14 626
[5 empty] | Construction management cost |  | 0 | 14 626
[5 empty] | Construction site labour costs |  | 5 321 | 0
|  |  |  | 35 Field construction supervision | Total |  | 16 282 | 175 006
[5 empty] | Construction management cost |  | 0 | 175 006
[5 empty] | Construction site labour costs |  | 16 282 | 0
|  |  |  | 36 Field indirect costs | Total |  | 217 834 | 355 848
[5 empty] | Construction: buildings, temp.: labour |  | 63 725 | 0
[5 empty] | Construction: buildings, temp.: materials |  | 0 | 10 226
[5 empty] | Construction: buildings, temp. facilities: labour |  | 133 846 | 0
[5 empty] | Construction buildings, temp. facilities: materials |  | 0 | 36 958
[5 empty] | Construction equip., major: labour |  | 17 664 | 0
[5 empty] | Construction equip., major: materials |  | 0 | 69 175
[5 empty] | Construction equip., small tools: labour costs |  | 571 | 0
[5 empty] | Construction equip., small tools: materials |  | 0 | 15 293
[5 empty] | Construction: expendable materials |  | 0 | 19 327
[5 empty] | Construction safety equip. inspection labour |  | 571 | 0
[5 empty] | Construction safety equip.: materials |  | 0 | 823
[5 empty] | Construction permits, insurance and local taxes |  | 0 | 27 156
[5 empty] | Construction field office labour expenses |  | 1 457 | 0
[5 empty] | Construction field office materials expenses |  | 0 | 27 629
[5 empty] | Construction payroll insurance and taxes |  | 0 | 149 261
|  |  |  | 37 Plant commissioning | Plant commissioning, total |  | 0 | 27 041
|  |  |  | MEASURING EMPLOYMENT GENERATED BY THE NUCLEAR POWER SECTOR, NEA No. 7204, © OECD 2018 |  |  |  |  | 69

## Third Table
COA | Component | NAICS Industry | CODE
223 | Accumulator tank (NSSS allocation) | Metal tank (heavy gauge) manufacturing | 332420
262 | Aerator and makeup system, auxiliary | Metal tank (heavy gauge) manufacturing | 332420
227 | Alarm system | Measuring and controlling device manufacturing | 334519
262 | Boiler blowdown, auxiliary | Power boiler and heat exchanger manufacturing | 332410
262 | Boiler, auxiliary feed water system | Power boiler and heat exchanger manufacturing | 332410
262 | Boiler, auxiliary system | Power boiler and heat exchanger manufacturing | 332410
223 | Boron injection system (NSSS allocation) | Power boiler and heat exchanger manufacturing | 332410
226 | Boron recycle system | Power boiler and heat exchanger manufacturing | 332410
210 | Building services | Power and related structures construction | 237130
262 | Chemical feed system, auxiliary | Metal tank (heavy gauge) manufacturing | 332420
264 | Chemical laboratory shop | Instruments and related products manufacturing | 334513
223 | Combustible gas control system | Instruments and related products manufacturing | 334513
263 | Communication: public address and intercom | Electrical and other wiring installation contractors | 238210
263 | Communication: telephone system | Electrical and other wiring installation contractors | 238210
212 | Concrete, interior | Concrete, poured structure contractors | 238110
262 | Condensate and steam return, auxiliary | Power boiler and heat exchanger manufacturing | 332410
233 | Condensate polishing | Power boiler and heat exchanger manufacturing | 332410
233 | Condensate system | Power boiler and heat exchanger manufacturing | 332410
233 | Condenser equip | Power boiler and heat exchanger manufacturing | 332410
233 | Condenser gas removal system | Power boiler and heat exchanger manufacturing | 332410
245 | Conduit: cable tray | Noncurrent-carrying wiring device manufacturing | 335932
245 | Conduit: miscellaneous | Noncurrent-carrying wiring device manufacturing | 335932
245 | Conduit: underground ducts (class 1E) | Noncurrent-carrying wiring device manufacturing | 335932
245 | Conduit: underground ducts (non-class 1E) | Noncurrent-carrying wiring device manufacturing | 335932
360 | Construction buildings, temp. facilities: materials | Labour, contracted | 561320
360 | Construction equip, major: labour | Labour, contracted | 561320
360 | Construction equip, major: materials | Power and related structures construction | 237130
360 | Construction equip, small tools: labour costs | Labour, contracted | 561320
360 | Construction equip, small tools: materials | Power and related structures construction | 237130
360 | Construction field office labour expenses | Labour, contracted | 561320
360 | Construction field office materials expenses | Power and related structures construction | 237130
300 | Construction management cost | Engineering services | 541330
360 | Construction payroll insurance and taxes | Insurance funds, other | 525190
360 | Construction permits, insurance and local taxes | Public finance activities (local) | 921130
360 | Construction safety equip: inspection | Labour, contracted | 561320
360 | Construction safety equip: materials | Power and related structures construction | 237130
300 | Construction site labour costs | Labour, contracted | 561320
360 | Construction: buildings, temporary facilities: labour | Labour, contracted | 561320
360 | Construction: buildings, temporary: labour | Labour, contracted | 561320
360 | Construction: buildings, temporary: materials | Power and related structures construction | 237130
360 | Construction: expendable materials | Power and related structures construction | 237130
227 | Containment atmosphere monitoring | Measuring and controlling device manufacturing | 334519
262 | Containment building instrument air system | Measuring and controlling device manufacturing | 334519
212 | Containment dome | Power and related structures construction | 237130
212 | Containment liner | Structural steel, fabricated, manufacturing | 332312
212 | Containment shell | Structural steel and precast concrete contractors | 238120
223 | Containment spray system | Industrial heating and cooling equipment manufacturing | 333415
221 | Control rod drive mechanism seismic supports (field cost) | Power boiler and heat exchanger manufacturing | 332410
221 | Control rod drive missile shield (field cost) | Power boiler and heat exchanger manufacturing | 332410
221 | Control rod drives (field cost) | Power boiler and heat exchanger manufacturing | 332410
221 | Control rod drives (NSSS allocation) | Power boiler and heat exchanger manufacturing | 332410
221 | Control rods (NSSS allocation) | Power boiler and heat exchanger manufacturing | 332410
252 | Cooling tower basins | Industrial heating and cooling equipment manufacturing | 333415
252 | Cooling tower makeup/blowdown system | Industrial heating and cooling equipment manufacturing | 333415
252 | Cooling towers | Industrial heating and cooling equipment manufacturing | 333415
251 | Cooling: circulating water pump house services | Pump and pumping equipment manufacturing | 333911
251 | Cooling: circulating water pump house structure | Power and related structures construction | 237130
252 | Cooling: circulating water system | Pump and pumping equipment manufacturing | 333911
251 | Cooling: makeup water intake structure | Pump and pumping equipment manufacturing | 333911
251 | Cooling: makeup water pre-treatment building | Pump and pumping equipment manufacturing | 333911
251 | Cooling: makeup water pre-treatment building services | Pump and pumping equipment manufacturing | 333911
252 | Cooling: water intake equip | Pump and pumping equipment manufacturing | 333911
261 | Cranes in diesel building | Crane, hoist and overhead travelling system manufacturing | 333923
261 | Cranes in heater bay | Crane, hoist and overhead travelling system manufacturing | 333923
261 | Cranes in reactor containment building | Crane, hoist and overhead travelling system manufacturing | 333923
261 | Cranes: misc. with hoists and monorails | Crane, hoist and overhead travelling system manufacturing | 333923
261 | Cranes: overhead in turbine building | Crane, hoist and overhead travelling system manufacturing | 333923
310 | Design of plant at home office, total | Engineering services | 541330
330 | Design services in field, total | Engineering services | 541330
241 | Diesel generator sequence logic panels | Instruments and related products manufacturing | 334513
242 | Diesel generator systems, emergency | Turbine and turbine generator set manufacturing | 333611
242 | Diesel generator systems, emergency TMI | Turbine and turbine generator set manufacturing | 333611
210 | Earthwork plus excavation work | Site preparation contractors | 238910
210 | Elevator | Elevator and moving stairway manufacturing | 333921
227 | Engineered safety feature actuation system | Measuring and controlling device manufacturing | 334519
264 | Environmental monitoring equipment | Instruments and related products manufacturing | 334513
228 | Equipment insulation | Building equipment contractors, other | 238290
227 | Failed fuel detection | Measuring and controlling device manufacturing | 334519
234 | Feed water heater vent and drain system | Pipe, iron and steel pipe and tube manufacturing | 331210
234 | Feed water heaters | Water treatment equipment manufacturing | 333318
234 | Feed water steam extraction system | Water treatment equipment manufacturing | 333318
234 | Feed water system | Pump and pumping equipment manufacturing | 333911
211 | Fencing and gates | Chain link fencing and fence gates | 332618
263 | Fire detection system, communications | Electrical and other wiring installation contractors | 238210
262 | Fire protection system | Fire detection and alarm systems manufacturing | 334290
222 | Fluid circulation drive (field cost) | Plumbing and HVAC contractors | 238220
262 | Fuel oil system, auxiliary | Metal tank (heavy gauge) manufacturing | 332420
262 | Fuel oil system, plant | Metal tank (heavy gauge) manufacturing | 332420
225 | Fuel storage, cleaning and inspection equipment | Measuring and controlling device manufacturing | 334519
264 | Furnishings and office equipment | Office furniture manufacturing | 337214
264 | Furnishings: change room equipment | Office furniture manufacturing | 337214
264 | Furnishings: dining facilities | Office furniture manufacturing | 337214
241 | Generator load break switch | Switchgear and switchboard apparatus manufacturing | 335313
241 | Generator neutral grounding equipment | Switchgear and switchboard apparatus manufacturing | 335313
243 | Generator protective relay panel | Switchgear and switchboard apparatus manufacturing | 335313
243 | Generator/auxiliary power system control panel | Switchgear and switchboard apparatus manufacturing | 335313
223 | Heat exchanger, residual heat removal (field cost) | Power and related structures construction | 237130
223 | Heat exchanger, residual heat removal (NSSS) | Power boiler and heat exchanger manufacturing | 332410
210 | HVAC | Plumbing and HVAC contractors | 238220
212 | HVAC (safety-related) | Plumbing and HVAC contractors | 238220
210 | HVAC (special) | Plumbing and HVAC contractors | 238220
227 | HVAC panels | Measuring and controlling device manufacturing | 334519
227 | Instrument racks | Measuring and controlling device manufacturing | 334519
227 | Instrumentation for accident monitoring | Measuring and controlling device manufacturing | 334519
210 | Lighting and service power | Electrical and other wiring installation contractors | 238210
227 | Logic panels | Measuring and controlling device manufacturing | 334519
320 | Management at home office, Including QA | Engineering services | 541330
262 | Misc. system: compressed air | Air compressors manufacturing | 333912
262 | Misc. system: potable water system | Water treatment equipment manufacturing | 333318
227 | Neutron monitoring | Measuring and controlling device manufacturing | 334519
227 | NSSS control board | Measuring and controlling device manufacturing | 334519
228 | NSSS Insulation | Building equipment contractors, other | 238290
200 | Painting, field | Painting engineered structures | 238320
228 | Pipe insulation | Building equipment contractors, other | 238290
222 | Piping, reactor coolant (field cost) | Power and related structures construction | 237130
222 | Piping, reactor coolant (NSSS allocation) | Pipe, iron and steel pipe and tube manufacturing | 331210
370 | Plant commissioning | Scientific and Technical Consulting Services | 541690
210 | Plumbing and drains | Metal products, all other misc. fabricated manufacturing | 332999
222 | Pressurising system (field cost) | Power and related structures construction | 237130
222 | Pressurizer (NSSS allocation) | Power boiler and heat exchanger manufacturing | 332410
222 | Pressurizer relief tank (NSSS allocation) | Metal tank (heavy gauge) manufacturing | 332420
227 | Process computer | Measuring and controlling device manufacturing | 334519
244 | Protection: cathodic | Electrical equipment and components, all other, manufacturing | 335999
244 | Protection: general station grounding system | Electrical equipment and components, all other, manufacturing | 335999
244 | Protection: heat tracing and freeze | Electrical equipment and components, all other, manufacturing | 335999
244 | Protection: lightning | Electrical equipment and components, all other, manufacturing | 335999
223 | Pumps and drives, residual heat removal (NSSS) | Pump and pumping equipment manufacturing | 333911
223 | Pumps and drives, safety injection system (field cost) | Pump and pumping equipment manufacturing | 333911
223 | Pumps and drives, safety injection system (NSSS) | Pump and pumping equipment manufacturing | 333911
200 | Qualification of welders | Welding, on-site, contractors | 238190
227 | Radiological monitoring | Measuring and controlling device manufacturing | 334519
224 | Radwaste equipment, miscellaneous | Other industrial machinery manufacturing | 333249
227 | Radwaste panels | Measuring and controlling device manufacturing | 334519
224 | Radwaste, gaseous (tritium) waste system | Other industrial machinery manufacturing | 333249
224 | Radwaste, solid, active dry volume reduction | Other industrial machinery manufacturing | 333249
211 | Railroads (hardware) | Heavy and other civil engineering construction | 237990
226 | Reactor chemical and volume control system | Instruments and related products manufacturing | 334513
226 | Reactor coolant treatment system | Water treatment equipment manufacturing | 333318
227 | Reactor diagnostic system | Measuring and controlling device manufacturing | 334519
226 | Reactor fluid leak detection system | Instruments and related products manufacturing | 334513
226 | Reactor inert gas system | Instruments and related products manufacturing | 334513
221 | Reactor lower internals (field cost) | Power and related structures construction | 237130
221 | Reactor lower internals (NSSS allocation) | Power boiler and heat exchanger manufacturing | 332410
226 | Reactor maintenance equip (NSSS and field cost) | Power boiler and heat exchanger manufacturing | 332410
226 | Reactor makeup water system | Pump and pumping equipment manufacturing | 333911
227 | Reactor plant I&C tubing | Noncurrent-carrying wiring device manufacturing | 335932
227 | Reactor power control | Measuring and controlling device manufacturing | 334519
226 | Reactor primary component cooling water | Pump and pumping equipment manufacturing | 333911
227 | Reactor protection system | Measuring and controlling device manufacturing | 334519
226 | Reactor sampling equipment | Instruments and related products manufacturing | 334513
226 | Reactor service water system | Pump and pumping equipment manufacturing | 333911
221 | Reactor supports (field cost) | Power and related structures construction | 237130
221 | Reactor upper internals (field cost) | Power and related structures construction | 237130
221 | Reactor upper internals (NSSS allocation) | Power boiler and heat exchanger manufacturing | 332410
221 | Reactor vessel structure (field cost) | Power and related structures construction | 237130
221 | Reactor vessel structure (NSSS allocation) | Power boiler and heat exchanger manufacturing | 332410
212 | Removable plugs | Metal products, all other misc. fabricated manufacturing | 332999
211 | Roads, walks and parking areas | Highway, street and bridge construction | 237310
211 | Roadway and yard lighting | Electrical and other wiring installation contractors | 238210
264 | Safety equipment | Instruments and related products manufacturing | 334513
211 | Sanitary sewer facilities | Water and sewer line and related structures construction | 237110
263 | Security system, communications | Electrical and other wiring installation contractors | 238210
262 | Service water system | Water treatment equipment manufacturing | 333318
211 | Settling basins | Power and related structures construction | 237130
227 | Standard NSSS valve package | Valve, industrial manufacturing | 332911
224 | Steam generator blowdown, liquid waste | Power boiler and heat exchanger manufacturing | 332410
222 | Steam generator equipment (field cost) | Power and related structures construction | 237130
222 | Steam generators (NSSS allocation) | Power boiler and heat exchanger manufacturing | 332410
262 | Steam system complete I&C, auxiliary | Instruments and related products manufacturing | 334513
212 | Structural and miscellaneous steel | Structural steel, fabricated, manufacturing | 332312
211 | Structure associated fill/backfill | Site preparation contractors | 238910
211 | Structure associated open cut | Site preparation contractors | 238910
241 | Switchgear: 13.8 kV (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
241 | Switchgear: 4.16 kV (class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
241 | Switchgear: 4.16 kV (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
241 | Switchgear: 480 V motor control (class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
241 | Switchgear: 480 V motor control (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
243 | Switchgear: AC distribution (class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
243 | Switchgear: AC distribution (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
242 | Switchgear: batteries (class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
242 | Switchgear: batteries (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
242 | Switchgear: charger (class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
242 | Switchgear: charger (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
243 | Switchgear: DC distribution (class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
243 | Switchgear: DC distribution (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
242 | Switchgear: inverters (class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
242 | Switchgear: inverters (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
242 | Switchgear: load centre (class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
242 | Switchgear: load centre (non-class 1E) | Switchgear and switchboard apparatus manufacturing | 335313
243 | Switchgear: misc. buttons, panels and fuses | Switchgear and switchboard apparatus manufacturing | 335313
243 | Switchgear: technical and on-site system control panels | Switchgear and switchboard apparatus manufacturing | 335313
227 | TMI instrumentation | Measuring and controlling device manufacturing | 334519
241 | Transformer: generator current and potential | Transformers, power and specialty, manufacturing | 335311
242 | Transformers: load centre (class 1E) | Transformers, power and specialty, manufacturing | 335311
242 | Transformers: load centre (non-class 1E) | Transformers, power and specialty, manufacturing | 335311
242 | Transformers: miscellaneous | Transformers, power and specialty, manufacturing | 335311
242 | Transformers: station service and start-up | Transformers, power and specialty, manufacturing | 335311
221 | Transport to site | Railroad line-haul | 482111
235 | Turbine auxiliaries | Turbine and turbine generator set manufacturing | 333611
233 | Turbine bypass system | Turbine and turbine generator set manufacturing | 333611
235 | Turbine chemical treatment system | Water treatment equipment manufacturing | 333318
235 | Turbine closed cooling water system | Water treatment equipment manufacturing | 333318
235 | Turbine demineralised water makeup system | Water treatment equipment manufacturing | 333318
231 | Turbine generator | Turbine and turbine generator set manufacturing | 333611
231 | Turbine generator CO2 storage system | Turbine and turbine generator set manufacturing | 333611
231 | Turbine generator hydrogen storage system | Turbine and turbine generator set manufacturing | 333611
231 | Turbine generator lubricating oil system | Turbine and turbine generator set manufacturing | 333611
231 | Turbine generator pedestal | Turbine and turbine generator set manufacturing | 333611
231 | Turbine generator reheater/moisture separator drain system and supports | Turbine and turbine generator set manufacturing | 333611
231 | Turbine generator, associated piping | Pipe, iron and steel pipe and tube manufacturing | 331210
231 | Turbine generator, other costs | Turbine and turbine generator set manufacturing | 333611
235 | Turbine main vapour piping system | Pipe, iron and steel pipe and tube manufacturing | 331210
235 | Turbine neutralisation system | Water treatment equipment manufacturing | 333318
236 | Turbine plant I&C tubing | Noncurrent-carrying wiring device manufacturing | 335932
237 | Turbine plant insulation | Building equipment contractors, other | 238290
224 | Waste train, liquid, chemical | Other industrial machinery manufacturing | 333249
224 | Waste train, liquid, chemical | Other industrial machinery manufacturing | 333249
224 | Waste train, liquid, detergent | Other industrial machinery manufacturing | 333249
224 | Waste train, liquid, detergent | Other industrial machinery manufacturing | 333249
224 | Waste train, liquid, miscellaneous | Other industrial machinery manufacturing | 333249
224 | Waste train, liquid, miscellaneous | Other industrial machinery manufacturing | 333249
224 | Waste train, regenerated chemical liquids | Other industrial machinery manufacturing | 333249
224 | Waste train, regenerated chemical liquids | Other industrial machinery manufacturing | 333249
224 | Waste, I&C | Instruments and related products manufacturing | 334513
224 | Waste, solid volume reduction system | Other industrial machinery manufacturing | 333249
265 | Wastewater treatment equipment | Water treatment equipment manufacturing | 333318
246 | Wiring and cables: containment penetrations | Electrical and other wiring installation contractors | 238210
246 | Wiring and cables: control cable | Electrical and other wiring installation contractors | 238210
246 | Wiring and cables: generator circuits wiring | Electrical and other wiring installation contractors | 238210
246 | Wiring and cables: instrument wire | Electrical and other wiring installation contractors | 238210
246 | Wiring and cables: station service power wiring | Electrical and other wiring installation contractors | 238210
211 | Yard drainage storm sewers | Water and sewer line and related structures construction | 237110